LASER INTERFEROMETER GRAVITATIONAL WAVE OBSERVATORY

- LIGO -

CALIFORNIA INSTITUTE OF TECHNOLOGY

MASSACHUSETTS INSTITUTE OF TECHNOLOGY

LIGO Laboratory / LIGO Scientific Collaboration

LIGO-T0900032-v1 2009-February-19

AdvLIGO Sample Clock Time Distribution System Final Design Review

R. Abbott, P. Fritschel, S. Waldman, and V. Sandberg (chair)

Distribution of this document:

Controls and Data Systems Group

This is an internal working note of the LIGO Project.

| California Institute of Technology LIGO Laboratory – MS 18-34 1200 E. California Blvd. Pasadena, CA 91125 Phone (626) 395-2129 FAX (626) 304-9834 e-mail: info@ligo.caltech.edu | Massachusetts Institute of Technology LIGO Laboratory – NW22-295 185 Albany St. Cambridge, MA 02139 Phone (617) 253-4824 FAX (617) 253-7014 e-mail: info@ligo.mit.edu |
| --- | --- |
| LIGO Hanford Observatory P. O. Box 159 Richland, WA 99352-0159 Phone (509) 372-8106 FAX (509) 372-8137 | LIGO Livingston Observatory P. O. Box 940 Livingston, LA 70754 Phone (225) 686-3100 FAX (225) 686-7189 |

http://www.ligo.caltech.edu

Document number and revision history:

DCC v2.0: LIGO-T0900032-v1	original	2009 February 19

Abstract

The Final Design Review of the "Sample Clock Time Distribution System" was completed successfully on February 19, 2009. The review determined the readiness for fabrication and verified that schematics, code, test plans, and related documentation were in place.

1.  Introduction

The Final Design Review of the "Sample Clock Time Distribution System" began January 28, 2009 and was completed successfully on February 19, 2009. The review determined the readiness for fabrication and verified that schematics, code, test plans, and related documentation were in place.  The previous  timing system reviews were the PDR (LIGO-T080271-00 ) held on 2008-March-28 and the CDR / DDR on 2005-May-02.

The LIGO interferometer control and data acquisition systems require a “clock” that provides stable and accurate timing signals for the converter sample rate generators that govern the analog-to-digital (ADC) and digital-to-analog (DAC)  converters and to provide a time-of-day signal to time stamp the acquired signals.  The generation and distribution of these timing signals are critical services for the operation of the interferometers.

The proposed system is documented in LIGO-E090003, which provides an overview.  The documentation list as prepared by the proposers is included as appendix A of this report.

2.  Review

The FDR was guided by the recommendations described in: “Guidelines for Advanced LIGO Detector Construction Activities,” M050220-09-D, 25 July 2008.  The review committee confirmed the check list shown below and accepted the test results as presented.

## Final Design Review Checklist:

Subsystem block and functional diagrams

Drawing package (assembly drawings and majority of remaining drawings)

Final parts lists

Design analysis and engineering test data

Software detailed design

Plans for acquisition of parts, components, materials needed for fabrication

Installation plans and procedures

Final hardware test plans

Final software test plans

Follow-up questions on the diagnostic capabilities of the system were answered in the documents referenced below:

LIGO-E0900036-v1:

Diagnostics Information for the Advanced LIGO Optical Timing

Distribution System

Abstract: In this document we describe diagnostics information transfer,

protocol and structure of the Advanced LIGO Optical Timing Distribution

System (OTD). We first review how data is collected and transferred from

the OTD to a remote computer. Next, we briefly discuss how data is

processed. We discuss in detail the structure of the collected data, as

it appears on a remote computer. Finally, we describe the status

information that is being collected. In the Appendix, we present an

example status information file.

LIGO-T0900050-v1:

Test Result Description Document for the Advanced LIGO Optical Timing Distribution System

Abstract: We present some test results that provide information on the proper operation of the OTD.

Follow-up information on phase noise and testing was answered by Daniel Sigg in an email (included below).

email from D. Sigg:

When a slave falls out of synchronization, it will detect this at the next 1 PPS marker. If a slave detects 8 misaligned 1 PPS markers in series it will re-synchronize automatically. This information is sent back to the fanout/master thorough the uplink port and then sent to the computer. All data transmissions are guarded with CRC values.

The software which collects the data on the computer exists. It uses DMT technology to make this information available as an XML file in a shared memory partition. We can watch this data by writing it to a file and see the information updating. However, an EPICS interface and an alarm manager are still on the TODO list.

One might ask the question: Are we catching all errors? Is it possible that we are missing data at the same time a synchronization error happens? Of course, this can happen easily. We protect against this by deploying error counters where needed (1-PPS-marker errors,  GPS errors, CRC errors, etc.). This way if some information is lost, one can check the  corresponding counter and see if it has increased. If so, this would be an indication of an  additional error.

Certainly more testing needs to be done. We are hopping to be able to set up a master in parallel with the current timing system during S6. This way we can get some long term exposure with a record on file.

3  Summary

The presentation and question session went very well.  The reviewers had no additional questions or comments and stated that the design looks very nice.   In summary,

"it is time to build the system."

Appendix - Timing FDR Web Page

http://lhocds.ligo-wa.caltech.edu:8000/advligo/Timing/TimingFDR

## CDS Converter Clock Timing System Final Design Review

- Meeting Dates and Times:

- Preliminary Discussion Thursday, February 5, 2009 9:00 PST

- Discussions with Presenters and Follow-up Questions Thursday, February 12, 2009 9:00 PST

- Final Discussion and Close Out Thursday, February 19, 2009

Documents and Links:

| 1 | Advanced LIGO Timing PDR Report | T080271 | local link |
| --- | --- | --- | --- |
| 2 | Main document map and overview: | E090003 | local link |
| 3 | Updated quick start guide: | E080541 | local link |

Integration Documents:

| 1 | Timing Slave: | E0900016 | local link |
| --- | --- | --- | --- |
| 2 | Clock, Gate, DuoTone: | E090001 | local link |
| 3 | Master/FanOut: | E090002 | local link |

Assembly and test procedures:

| 1 | Master/Fanout Assembly | D080534 | local link |
| --- | --- | --- | --- |
| 2 | Master/Fanout Test Plan | T080083 | local link |
| 3 | DuoTone Assembly | E0900019 | local link |
| 4 | Timing Slave Test Plan | E050262 | local link |

Test Results:

| 1 | Diagnostic Information | E0900036 | local link |
| --- | --- | --- | --- |
| 2 | Test Results | T0900050 | local link |