## notes
CABLE LENGTHS, CORNER STATION, H1 & H2
Cable lengths are based on D1002404-v4
D1002704, Rack and Cable Tray Layout, LVEA, H1 H2
Cable lengths to racks are the worksheets are to the bottom of the rack (coming in from above the rack).
Lengths are given from the 3 entry/exit points for cable trays into/out-of the LVEA (points A & B for H1 and point C for H2).
Lengths from racks in the LVEA to their associated chamber or equipment are not (yet) listed, but can be obtained from looking at Drawing D1002704
Cable lengths have an added margin of 10 feet, or 5%, whichever is largest.
The chamber designations for aLIGO are given in the files for LHO and LLO respectively:
D0901477-v2 file, Vacuum Chamber Designations for LHO aLIGO
D0901490-v1 file, Vacuum Chamber Designations for LLO aLIGO
The designations (naming conventions) for the feedthrough ports (optical and electrical) are given in these drawings:
D980227-x0, Naming Conventions, BSC Ports
D980226-x0, Naming Conventions for Ports on HAM Chamber
D980228-x0, Naming Conventions for Ports on Adapter
The orientation of the chambers (0 degree and support tubes for BSC chambers; orientation of the large bellows on the HAM chamber), is given in the following iLIGO drawings for LHO:
D961165-v1, LIGO Vacuum Equipment Arrangement Plan, Corner Station, Washington Site
D961169-v1, LIGO Vacuum Equipment Arrangement Plan, X-End Station, Washington Site
D961171-v1, LIGO Vacuum Equipment Arrangement Plan, Y-End Station, Washington Site
and for iLIGO LLO in these drawings:
D970383-v1, LIGO Vacuum Equipment Arrangement Plan, Corner Station, Louisiana Site
D970384-v1, LIGO Vacuum Equipment Arrangement Plan, X-End Station, Louisiana Site
D970385-v1, LIGO Vacuum Equipment Arrangement Plan, Y-End Station, Louisiana Site
In aLIGO, the BSC chambers in the corner stations and end stations of both observatories are not moved, so the orientation is the same as in iLIGO. However, at LHO the chambers from the mid-station are relocated to the end stations as H2 end test mass chambers. The orientation of these H2 end chambers will be the same as the H1 end chambers. The HAM chambers are all oriented so that the large bellows is always toward the vertex.
See also
D0901469-v5, aLIGO LHO X-End Layout
D0901467-v5, aLIGO LHO Y-End Layout

## H1 - pt A to LVEA
H1 - POINT A TO LVEA LOCATIONS |  |  |  | length margin = | 5% | or | 120 | inches, whichever is longer
|  | LENGTH (ft) |  | bend radius = | 12
POINT | RACK or PORT or SITE | BASIC | with margin | # 90 deg BENDS | intermediate lengths in inches:
A | SUS-H1-R1 | 56.104 | 66 | 5 | 58 | 206 | 283 | 32 | 120
A | WMCA1 ports | 60.7323 | 70 | 3 | 58 | 206 | 299 | 48 | 17 | 116.2389
A | WHAM2, port D1 | 59.483 | 69 | 8 | 58 | 206 | 283 | 115 | 57 | 36
A | WHAM2, port D2 | 61.5664 | 71 | 8 | 58 | 206 | 283 | 115 | 57 | 33 | 28
A | WHAM2, port D3 | 64.983 | 74 | 8 | 58 | 206 | 283 | 115 | 57 | 66 | 36
A | WHAM2, port D4 | 72.458 | 82 | 10 | 58 | 206 | 283 | 115 | 57 | 66 | 100 | 36
A | WHAM2, port D5 | 74.5413 | 84 | 10 | 58 | 206 | 283 | 115 | 57 | 66 | 100 | 33 | 28
A | WHAM2, port D6 | 77.958 | 87 | 10 | 58 | 206 | 283 | 115 | 57 | 66 | 100 | 66 | 36
A | WHAM1, port D1 | 67.3872 | 77 | 9 | 58 | 206 | 283 | 115 | 57 | 100 | 36
A | WHAM1, port D2 | 69.4705 | 79 | 9 | 58 | 206 | 283 | 115 | 57 | 100 | 33 | 28
A | WHAM1, port D3 | 72.8872 | 82 | 9 | 58 | 206 | 283 | 115 | 57 | 100 | 66 | 36
A | WHAM1, port D4 | 80.7913 | 90 | 10 | 58 | 206 | 283 | 115 | 57 | 100 | 66 | 100 | 36
A | WHAM1, port D5 | 82.8746 | 92 | 10 | 58 | 206 | 283 | 115 | 57 | 100 | 66 | 100 | 33 | 28
A | WHAM1, port D6 | 86.2913 | 96 | 10 | 58 | 206 | 283 | 115 | 57 | 100 | 66 | 100 | 66 | 36
A | ISC-H1-R2 | 96.7581 | 106 | 6 | 58 | 206 | 299 | 48 | 279 | 146 | 12 | 24 | 120
A | ISC-H1-R1 | 101.9248 | 111 | 6 | 58 | 206 | 299 | 48 | 279 | 146 | 12 | 24 | 38 | 24 | 120
A | PSL-H1-R2 | 107.0914 | 117 | 6 | 58 | 206 | 299 | 48 | 279 | 146 | 12 | 24 | 38 | 24 | 38 | 24 | 120
A | PSL-H1-R1 | 112.2581 | 122 | 6 | 58 | 206 | 299 | 48 | 279 | 146 | 12 | 24 | 38 | 24 | 38 | 24 | 38 | 24 | 120
A | SEI-H1-G1 | 117.3289 | 127 | 7 | 58 | 206 | 299 | 48 | 279 | 146 | 249 | 120 | 39
A | PSL-H1-T1 | 116.7456 | 126 | 7 | 58 | 206 | 299 | 48 | 267 | 115 | 241 | 48 | 59 | 96
A | SUS-H1-R2 | 40.7706 | 50 | 5 | 58 | 206 | 99 | 32 | 120
A | WMCB1 ports | 44.7198 | 54 | 4 | 58 | 206 | 109 | 50 | 18 | 116.2389
A | WHAM3, port D1 | 57.3038 | 67 | 9 | 58 | 206 | 99 | 32 | 33 | 115 | 55 | 100 | 36
A | WHAM3, port D2 | 59.0538 | 69 | 9 | 58 | 206 | 99 | 32 | 33 | 115 | 51 | 100 | 33 | 28
A | WHAM3, port D3 | 62.4705 | 72 | 9 | 58 | 206 | 99 | 32 | 33 | 115 | 51 | 100 | 66 | 36
A | WHAM3, port D4 | 49.0664 | 59 | 8 | 58 | 206 | 99 | 32 | 33 | 115 | 51 | 36
A | WHAM3, port D5 | 51.1497 | 61 | 8 | 58 | 206 | 99 | 32 | 33 | 115 | 51 | 33 | 28
A | WHAM3, port D6 | 54.5664 | 64 | 8 | 58 | 206 | 99 | 32 | 33 | 115 | 51 | 66 | 36
A | WBSC2, far side, E & F ports | 64.729 | 74 | 4 | 58 | 206 | 109 | 50 | 168 | 10 | 196.3495
A | WBSC2, far side, G ports | 69.1748 | 79 | 5 | 58 | 206 | 109 | 50 | 168 | 10 | 196.3495 | 58.5
A | WBSC3, far side, E & F ports | 85.5664 | 95 | 6 | 58 | 206 | 109 | 50 | 168 | 10 | 196.3495 | 64 | 196.3495
A | WBSC3, far side,G ports | 90.0122 | 100 | 7 | 58 | 206 | 109 | 50 | 168 | 10 | 196.3495 | 64 | 196.3495 | 58.5
A | SUS-H1-R5 | 101.3903 | 111 | 8 | 58 | 206 | 109 | 50 | 168 | 10 | 196.3495 | 64 | 102.5381 | 78 | 96 | 120
A | TCS-H1-R1 | 75.5352 | 85 | 8 | 58 | 206 | 109 | 50 | 168 | 10 | 139.6263 | 29 | 58 | 120
A | TCS-H1-R2 | 89.9956 | 99 | 7 | 58 | 206 | 235 | 219 | 109 | 70 | 99 | 120
A | SUS-H1-R6 | 91.1435 | 101 | 9 | 58 | 206 | 109 | 50 | 168 | 10 | 101.4473 | 65 | 103.6289 | 72 | 77 | 120
A | SEI-H1-G3 | 95.3102 | 105 | 9 | 58 | 206 | 109 | 50 | 168 | 10 | 101.4473 | 65 | 103.6289 | 72 | 127 | 120
A | WBSC1, far side, E & F ports | 77.7412 | 87 | 6 | 58 | 206 | 109 | 50 | 168 | 10 | 101.4473 | 65 | 196.3495
A | WBSC1, far side, G ports | 82.187 | 92 | 7 | 58 | 206 | 109 | 50 | 168 | 10 | 101.4473 | 65 | 196.3495 | 58.5
A | OPLEV-H1-Y1 | 192.8562 | 202 | 9 | 58 | 206 | 235 | 219 | 109 | 99 | 103.6289 | 58 | 43 | 950 | 121 | 39 | 120

## H1 - pt A to Rack Room
H1 - POINT A TO RACK ROOM |  |  |  | length margin = | 5% | or | 120 | inches, whichever is longer
|  | LENGTH (ft) |  | bend radius = | 12
POINT | RACK | BASIC | with margin | # 90 deg BENDS | intermediate lengths in inches:
A | H1-PSL-C1 | 21.2957 | 31 | 3 | 97 | 35 | 19 | 120
A | H1-UNK-C4 | 23.2957 | 33 | 3 | 97 | 35 | 19 | 24 | 120
A | H1-UNK-C5 | 25.2957 | 35 | 3 | 97 | 35 | 19 | 24 | 24 | 120
A | H1-AOS-C1 | 27.2957 | 37 | 3 | 97 | 35 | 19 | 24 | 24 | 24 | 120
A | H1-SEI-C1 | 32.7124 | 42 | 3 | 97 | 35 | 156 | 120
A | H1-SEI-C2 | 34.7124 | 44 | 3 | 97 | 35 | 156 | 24 | 120
A | H1-SEI-C3 | 36.7124 | 46 | 3 | 97 | 35 | 156 | 24 | 24 | 120
A | H1-SEI-C4 | 38.7124 | 48 | 3 | 97 | 35 | 156 | 24 | 24 | 24 | 120
A | H1-SEI-C5 | 40.7124 | 50 | 3 | 97 | 35 | 156 | 24 | 24 | 24 | 24 | 120
A | H1-SEI-C6 | 42.7124 | 52 | 3 | 97 | 35 | 156 | 24 | 24 | 24 | 24 | 24 | 120
A | H1-SUS-C4 | 20.8083 | 30 | 2 | 97 | 43 | 120
A | H1-SUS-C3 | 22.8083 | 32 | 2 | 97 | 43 | 24 | 120
A | H1-SUS-C2 | 24.8083 | 34 | 2 | 97 | 43 | 24 | 24 | 120
A | H1-SUS-C1 | 26.8083 | 36 | 2 | 97 | 43 | 24 | 24 | 24 | 120
A | H1-SUS-C5 | 35.3665 | 45 | 4 | 97 | 82 | 98 | 24 | 24 | 120
A | H1-SUS-C6 | 33.3665 | 43 | 4 | 97 | 82 | 98 | 24 | 120
A | H1-SUS-C7 | 31.7957 | 41 | 3 | 97 | 82 | 98 | 120
A | H1-SUS-C8 | 33.3665 | 43 | 4 | 97 | 82 | 98 | 24 | 120
A | H1-PEM-C1 | 41.8665 | 51 | 4 | 97 | 82 | 176 | 24 | 24 | 120
A | H1-UNK-C3 | 39.8665 | 49 | 4 | 97 | 82 | 176 | 24 | 120
A | H1-UNK-C2 | 38.2957 | 48 | 3 | 97 | 82 | 176 | 120
A | H1-UNK-C1 | 39.8665 | 49 | 4 | 97 | 82 | 176 | 24 | 120
A | H1-ISC-C1 | 49.3665 | 59 | 4 | 97 | 82 | 266 | 24 | 24 | 120
A | H1-ISC-C2 | 47.3665 | 57 | 4 | 97 | 82 | 266 | 24 | 120
A | H1-ISC-C3 | 45.7957 | 55 | 3 | 97 | 82 | 266 | 120
A | H2-LDR-C1 | 54.1165 | 64 | 4 | 97 | 35 | 394 | 24 | 120
A | H1-LDR-C2 | 52.5457 | 62 | 3 | 97 | 35 | 394 | 120
A | H1-LDR-C1 | 54.1165 | 64 | 4 | 97 | 35 | 394 | 24 | 120
A | H1-VDC-C1 | 33.4373 | 43 | 5 | 156 | 97 | 35 | 19 | 120
A | H1-VDC-C2 | 35.4373 | 45 | 5 | 156 | 97 | 35 | 19 | 24 | 120
A | H1-VDC-C3 | 37.4373 | 47 | 5 | 156 | 97 | 35 | 19 | 24 | 24 | 120
A | H1-VDC-C4 | 39.4373 | 49 | 5 | 156 | 97 | 35 | 19 | 24 | 24 | 24 | 120

## H1 - pt B to LVEA
H1 - POINT B TO LVEA LOCATIONS |  |  |  | length margin = | 5% | or | 120
|  | LENGTH (ft) |  | bend radius = | 12
POINT | RACK or PORT or SITE | BASIC | with margin | # 90 deg BENDS | intermediate lengths in inches:
B | SUS-H1-R3 | 34.4624 | 44 | 3 | 217 | 60 | 32 | 120
B | WMCB2 ports | 37.5782 | 47 | 2 | 217 | 67 | 43 | 18 | 116.2389
B | WHAM4, port D1 | 56.8289 | 66 | 7 | 217 | 60 | 32 | 42 | 115 | 50 | 100 | 66 | 36
B | WHAM4, port D2 | 53.4122 | 63 | 7 | 217 | 60 | 32 | 42 | 115 | 50 | 100 | 33 | 28
B | WHAM4, port D3 | 51.3289 | 61 | 7 | 217 | 60 | 32 | 42 | 115 | 50 | 100 | 36
B | WHAM4, port D4 | 43.4248 | 53 | 6 | 217 | 60 | 32 | 42 | 115 | 50 | 36
B | WHAM4, port D5 | 45.5081 | 55 | 6 | 217 | 60 | 32 | 42 | 115 | 50 | 33 | 28
B | WHAM4, port D6 | 48.9248 | 58 | 6 | 217 | 60 | 32 | 42 | 115 | 50 | 66 | 36
B | TCS-H1-R1 | 53.2957 | 63 | 3 | 217 | 67 | 43 | 150 | 58 | 120
B | WBSC2, far side, E & F ports | 58.4749 | 68 | 2 | 217 | 67 | 43 | 179 | 10 | 196
B | WBSC2, far side, G ports | 62.9624 | 72 | 3 | 217 | 67 | 43 | 179 | 10 | 196 | 59
B | WBSC3, far side, E & F ports | 71.2832 | 81 | 4 | 217 | 67 | 43 | 179 | 10 | 100 | 64 | 196
B | WBSC3, far side,G ports | 75.7706 | 85 | 5 | 217 | 67 | 43 | 179 | 10 | 100 | 64 | 196 | 59
B | SUS-H1-R5 | 86.6622 | 96 | 7 | 217 | 67 | 43 | 179 | 10 | 100 | 64 | 102 | 78 | 96 | 120
B | H1-TCS-CHILLER | 94.854 | 104 | 5 | 217 | 162 | 252 | 61 | 352 | 120
B | WMCA2 ports | 58.9948 | 68 | 2 | 217 | 318 | 49 | 18 | 116.2389
B | WHAM5, port D1 | 67.1622 | 77 | 7 | 217 | 370 | 115 | 38 | 66 | 36
B | WHAM5, port D2 | 63.7456 | 73 | 7 | 217 | 370 | 115 | 38 | 33 | 28
B | WHAM5, port D3 | 61.6622 | 71 | 7 | 217 | 370 | 115 | 38 | 36
B | WHAM5, port D4 | 69.9956 | 79 | 7 | 217 | 370 | 115 | 38 | 100 | 36
B | WHAM5, port D5 | 72.0789 | 82 | 7 | 217 | 370 | 115 | 38 | 100 | 33 | 28
B | WHAM5, port D6 | 75.4956 | 85 | 7 | 217 | 370 | 115 | 38 | 100 | 66 | 36
B | WHAM6, port D1 | 75.4956 | 85 | 7 | 217 | 370 | 115 | 38 | 100 | 66 | 36
B | WHAM6, port D2 | 72.0789 | 82 | 7 | 217 | 370 | 115 | 38 | 100 | 33 | 28
B | WHAM6, port D3 | 69.9956 | 79 | 7 | 217 | 370 | 115 | 38 | 100 | 36
B | WHAM6, port D4 | 78.3289 | 88 | 7 | 217 | 370 | 115 | 38 | 200 | 36
B | WHAM6, port D5 | 80.4122 | 90 | 7 | 217 | 370 | 115 | 38 | 200 | 33 | 28
B | WHAM6, port D6 | 83.8289 | 93 | 7 | 217 | 370 | 115 | 38 | 200 | 66 | 36
B | ISC-H1-R3 | 85.8916 | 95 | 2 | 217 | 318 | 49 | 337 | 120
B | SUS-H1-R4 | 88.1416 | 98 | 2 | 217 | 318 | 49 | 364 | 120
B | SEI-GND-H1-2 | 92.0583 | 102 | 2 | 217 | 318 | 49 | 411 | 120
B | OPLEV-H1-X1 | 206.7537 | 217 | 13 | 217 | 67 | 43 | 168 | 10 | 100 | 64 | 102 | 78 | 96 | 24 | 65 | 94 | 100 | 28 | 32 | 993 | 107 | 40 | 120

## H1 - pt B to Rack Room
H1 - POINT B TO RACK ROOM |  |  |  | length margin = | 5% | or | 120 | inches, whichever is longer
|  | LENGTH (ft) |  | bend radius = | 12
POINT | RACK | BASIC | with margin | # 90 deg BENDS | intermediate lengths in inches:
B | H1-PSL-C1 | 24.7249 | 34 | 2 | 115 | 24 | 24 | 24 | 120
B | H1-UNK-C4 | 22.7249 | 32 | 2 | 115 | 24 | 24 | 120
B | H1-UNK-C5 | 20.7249 | 30 | 2 | 115 | 24 | 120
B | H1-AOS-C1 | 19.1541 | 29 | 1 | 115 | 120
B | H1-SEI-C1 | 24.1416 | 34 | 2 | 115 | 65 | 120
B | H1-SEI-C2 | 26.1416 | 36 | 2 | 115 | 65 | 24 | 120
B | H1-SEI-C3 | 28.1416 | 38 | 2 | 115 | 65 | 24 | 24 | 120
B | H1-SEI-C4 | 30.1416 | 40 | 2 | 115 | 65 | 24 | 24 | 24 | 120
B | H1-SEI-C5 | 32.1416 | 42 | 2 | 115 | 65 | 24 | 24 | 24 | 24 | 120
B | H1-SEI-C6 | 34.1416 | 44 | 2 | 115 | 65 | 24 | 24 | 24 | 24 | 24 | 120
B | H1-SUS-C4 | 31.5457 | 41 | 3 | 115 | 81 | 35 | 43 | 120
B | H1-SUS-C3 | 33.5457 | 43 | 3 | 115 | 81 | 35 | 43 | 24 | 120
B | H1-SUS-C2 | 34.7957 | 44 | 3 | 115 | 81 | 35 | 82 | 120
B | H1-SUS-C1 | 36.7957 | 46 | 3 | 115 | 81 | 35 | 82 | 24 | 120
B | H1-SUS-C5 | 26.2124 | 36 | 3 | 115 | 17 | 35 | 43 | 120
B | H1-SUS-C6 | 28.2124 | 38 | 3 | 115 | 17 | 35 | 43 | 24 | 120
B | H1-SUS-C7 | 30.2124 | 40 | 3 | 115 | 17 | 35 | 43 | 24 | 24 | 120
B | H1-SUS-C8 | 32.2124 | 42 | 3 | 115 | 17 | 35 | 43 | 24 | 24 | 24 | 120
B | H1-PEM-C1 | 32.7124 | 42 | 3 | 115 | 95 | 35 | 43 | 120
B | H1-UNK-C3 | 34.7124 | 44 | 3 | 115 | 95 | 35 | 43 | 24 | 120
B | H1-UNK-C2 | 36.7124 | 46 | 3 | 115 | 95 | 35 | 43 | 24 | 24 | 120
B | H1-UNK-C1 | 38.7124 | 48 | 3 | 115 | 95 | 35 | 43 | 24 | 24 | 24 | 120
B | H1-ISC-C1 | 40.2124 | 50 | 3 | 115 | 185 | 35 | 43 | 120
B | H1-ISC-C2 | 42.2124 | 52 | 3 | 115 | 185 | 35 | 43 | 24 | 120
B | H1-ISC-C3 | 44.2124 | 54 | 3 | 115 | 185 | 35 | 43 | 24 | 24 | 120
B | H2-LDR-C1 | 46.3791 | 56 | 3 | 115 | 313 | 24 | 120
B | H1-LDR-C2 | 44.8083 | 54 | 2 | 115 | 313 | 120
B | H1-LDR-C1 | 46.3791 | 56 | 3 | 115 | 313 | 24 | 120
A | H1-VDC-C1 | 36.8665 | 46 | 4 | 156 | 115 | 24 | 24 | 24 | 120
A | H1-VDC-C2 | 34.8665 | 44 | 4 | 156 | 115 | 24 | 24 | 120
A | H1-VDC-C3 | 32.8665 | 42 | 4 | 156 | 115 | 24 | 120
A | H1-VDC-C4 | 31.2957 | 41 | 3 | 156 | 115 | 120

## H1 - LVEA rack to chamber
H1 - LVEA RACK TO CHAMBER/TABLE |  |  |  | length margin = | 5% | or | 120 | inches, whichever is longer
|  | LENGTH (ft) |  | bend radius = | 12
RACK | CHAMBER/TABLE | BASIC | with margin | # 90 deg BENDS | intermediate lengths in inches:
ISC-H1-R1 | H1-ISCHT1 | 31.6999 | 41 | 4 | 120 | 24 | 38 | 24 | 12 | 52 | 47 | 84
ISC-H1-R1 | WHAM1, port D1 | 49.4373 | 59 | 5 | 120 | 24 | 38 | 24 | 12 | 84 | 115 | 66 | 100 | 36
ISC-H1-R1 | WHAM1, port D2 | 51.5206 | 61 | 5 | 120 | 24 | 38 | 24 | 12 | 84 | 115 | 66 | 100 | 33 | 28
ISC-H1-R1 | WHAM1, port D3 | 54.9373 | 64 | 5 | 120 | 24 | 38 | 24 | 12 | 84 | 115 | 66 | 100 | 66 | 36
ISC-H1-R1 | WHAM1, port D4 | 46.604 | 56 | 5 | 120 | 24 | 38 | 24 | 12 | 84 | 115 | 66 | 66 | 36
ISC-H1-R1 | WHAM1, port D5 | 43.1873 | 53 | 5 | 120 | 24 | 38 | 24 | 12 | 84 | 115 | 66 | 33 | 28
ISC-H1-R1 | WHAM1, port D6 | 41.104 | 51 | 5 | 120 | 24 | 38 | 24 | 12 | 84 | 115 | 66 | 36
ISC-H1-R2 | H1-ISCHT1 | 26.5332 | 36 | 4 | 120 | 24 | 12 | 52 | 47 | 84
ISC-H1-R2 | WHAM1, port D1 | 44.2706 | 54 | 5 | 120 | 24 | 12 | 84 | 115 | 66 | 100 | 36
ISC-H1-R2 | WHAM1, port D2 | 46.354 | 56 | 5 | 120 | 24 | 12 | 84 | 115 | 66 | 100 | 33 | 28
ISC-H1-R2 | WHAM1, port D3 | 49.7706 | 59 | 5 | 120 | 24 | 12 | 84 | 115 | 66 | 100 | 66 | 36
ISC-H1-R2 | WHAM1, port D4 | 41.4373 | 51 | 5 | 120 | 24 | 12 | 84 | 115 | 66 | 66 | 36
ISC-H1-R2 | WHAM1, port D5 | 38.0206 | 48 | 5 | 120 | 24 | 12 | 84 | 115 | 66 | 33 | 28
ISC-H1-R2 | WHAM1, port D6 | 35.9373 | 45 | 5 | 120 | 24 | 12 | 84 | 115 | 66 | 36
SUS-H1-R1 | WHAM2, port D1 | 29.6999 | 39 | 4 | 120 | 49 | 115 | 57 | 36
SUS-H1-R1 | WHAM2, port D2 | 31.7832 | 41 | 4 | 120 | 49 | 115 | 57 | 33 | 28
SUS-H1-R1 | WHAM2, port D3 | 35.1999 | 45 | 4 | 120 | 49 | 115 | 57 | 66 | 36
SUS-H1-R1 | WHAM2, port D4 | 43.5332 | 53 | 4 | 120 | 49 | 115 | 57 | 100 | 66 | 36
SUS-H1-R1 | WHAM2, port D5 | 40.1165 | 50 | 4 | 120 | 49 | 115 | 57 | 100 | 33 | 28
SUS-H1-R1 | WHAM2, port D6 | 38.0332 | 48 | 4 | 120 | 49 | 115 | 57 | 100 | 36
SUS-H1-R2 | WHAM3, port D1 | 36.5332 | 46 | 4 | 120 | 33 | 115 | 55 | 100 | 36
SUS-H1-R2 | WHAM3, port D2 | 38.6165 | 48 | 4 | 120 | 33 | 115 | 55 | 100 | 33 | 28
SUS-H1-R2 | WHAM3, port D3 | 42.0332 | 52 | 4 | 120 | 33 | 115 | 55 | 100 | 66 | 36
SUS-H1-R2 | WHAM3, port D4 | 33.6999 | 43 | 4 | 120 | 33 | 115 | 55 | 66 | 36
SUS-H1-R2 | WHAM3, port D5 | 30.2832 | 40 | 4 | 120 | 33 | 115 | 55 | 33 | 28
SUS-H1-R2 | WHAM3, port D6 | 28.1999 | 38 | 4 | 120 | 33 | 115 | 55 | 36
TCS-H1-R1 | H1-TCSHT4R | 29.3665 | 39 | 4 | 120 | 30 | 115 | 60 | 48
TCS-H1-R1 | H1-TCSX | 49.5789 | 59 | 7 | 120 | 58 | 29 | 100 | 64 | 146 | 30 | 84
SUS-H1-R3 | WHAM4, port D1 | 42.3665 | 52 | 4 | 120 | 42 | 115 | 50 | 100 | 66 | 36
SUS-H1-R3 | WHAM4, port D2 | 38.9499 | 48 | 4 | 120 | 42 | 115 | 50 | 100 | 33 | 28
SUS-H1-R3 | WHAM4, port D3 | 36.8665 | 46 | 4 | 120 | 42 | 115 | 50 | 100 | 36
SUS-H1-R3 | WHAM4, port D4 | 28.5332 | 38 | 4 | 120 | 42 | 115 | 50 | 36
SUS-H1-R3 | WHAM4, port D5 | 30.6165 | 40 | 4 | 120 | 42 | 115 | 50 | 33 | 28
SUS-H1-R3 | WHAM4, port D6 | 34.0332 | 44 | 4 | 120 | 42 | 115 | 50 | 66 | 36
ISC-H1-R3 | WHAM6, port D1 | 42.3665 | 52 | 4 | 120 | 62 | 115 | 30 | 100 | 66 | 36
ISC-H1-R3 | WHAM6, port D2 | 38.9499 | 48 | 4 | 120 | 62 | 115 | 30 | 100 | 33 | 28
ISC-H1-R3 | WHAM6, port D3 | 36.8665 | 46 | 4 | 120 | 62 | 115 | 30 | 100 | 36
ISC-H1-R3 | WHAM6, port D4 | 28.5332 | 38 | 4 | 120 | 62 | 115 | 30 | 36
ISC-H1-R3 | WHAM6, port D5 | 30.6165 | 40 | 4 | 120 | 62 | 115 | 30 | 33 | 28
ISC-H1-R3 | WHAM6, port D6 | 34.0332 | 44 | 4 | 120 | 62 | 115 | 30 | 66 | 36
SUS-H1-R4 | WHAM5, port D1 | 52.9499 | 62 | 4 | 120 | 89 | 115 | 30 | 200 | 66 | 36
SUS-H1-R4 | WHAM5, port D2 | 49.5332 | 59 | 4 | 120 | 89 | 115 | 30 | 200 | 33 | 28
SUS-H1-R4 | WHAM5, port D3 | 47.4499 | 57 | 4 | 120 | 89 | 115 | 30 | 200 | 36
SUS-H1-R4 | WHAM5, port D4 | 39.1165 | 49 | 4 | 120 | 89 | 115 | 30 | 100 | 36
SUS-H1-R4 | WHAM5, port D5 | 41.1999 | 51 | 4 | 120 | 89 | 115 | 30 | 100 | 33 | 28
SUS-H1-R4 | WHAM5, port D6 | 44.6165 | 54 | 4 | 120 | 89 | 115 | 30 | 100 | 66 | 36
SUS-H1-R4 | WHAM6, port D1 | 44.6165 | 54 | 4 | 120 | 89 | 115 | 30 | 100 | 66 | 36
SUS-H1-R4 | WHAM6, port D2 | 41.1999 | 51 | 4 | 120 | 89 | 115 | 30 | 100 | 33 | 28
SUS-H1-R4 | WHAM6, port D3 | 39.1165 | 49 | 4 | 120 | 89 | 115 | 30 | 100 | 36
SUS-H1-R4 | WHAM6, port D4 | 30.7832 | 40 | 4 | 120 | 89 | 115 | 30 | 36
SUS-H1-R4 | WHAM6, port D5 | 32.8665 | 42 | 4 | 120 | 89 | 115 | 30 | 33 | 28
SUS-H1-R4 | WHAM6, port D6 | 36.2832 | 46 | 4 | 120 | 89 | 115 | 30 | 66 | 36
SUS-H1-R5 | WBSC2, far side, E & F ports | 69.0883 | 79 | 3 | 120 | 96 | 78 | 290.161 | 64 | 196.3495
SUS-H1-R5 | WBSC3, far side, E & F ports | 39.5749 | 49 | 3 | 120 | 96 | 78 | 196.3495
SUS-H1-R6 | WBSC1, far side, E & F ports | 37.4915 | 47 | 3 | 120 | 77 | 72 | 196.3495
SUS-H1-R6 | WBSC2, far side, E & F ports | 66.139 | 76 | 5 | 120 | 77 | 72 | 289.0702 | 65 | 196.3495
TCS-H1-R2 | H1-TCSY | 20.0583 | 30 | 2 | 120 | 24 | 23 | 84

## H2 - pt C to LVEA
H2 - POINT C TO LVEA LOCATIONS |  |  |  | length margin = | 5% | or | 120 | inches, whichever is longer
|  | LENGTH (ft) |  | bend radius = | 12
POINT | RACK or PORT or SITE | BASIC | with margin | # 90 deg BENDS | intermediate lengths in inches:
C | SUS-H2-R1 | 154.5206 | 164 | 5 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 120
C | WMCA3 ports | 158.8031 | 168 | 4 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 64 | 18 | 116.2389
C | WHAM8, port D1 | 164.3164 | 174 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 36
C | WHAM8, port D2 | 166.3997 | 176 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 33 | 28
C | WHAM8, port D3 | 169.8164 | 179 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 66 | 36
C | WHAM8, port D4 | 178.1497 | 188 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 100 | 66 | 36
C | WHAM8, port D5 | 174.733 | 184 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 100 | 33 | 28
C | WHAM8, port D6 | 172.6497 | 182 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 100 | 36
C | WHAM7, port D1 | 172.6497 | 182 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 100 | 36
C | WHAM7, port D2 | 174.733 | 184 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 100 | 33 | 28
C | WHAM7, port D3 | 178.1497 | 188 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 100 | 66 | 36
C | WHAM7, port D4 | 186.483 | 196 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 200 | 66 | 36
C | WHAM7, port D5 | 183.0664 | 193 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 200 | 33 | 28
C | WHAM7, port D6 | 180.983 | 190 | 8 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 32 | 50 | 115 | 52 | 200 | 36
C | ISC-H2-R2 | 194.5081 | 204 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 64 | 270 | 153 | 6 | 24 | 120
C | ISC-H2-R1 | 199.6748 | 209 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 64 | 270 | 153 | 6 | 24 | 38 | 24 | 120
C | PSL-H2-R2 | 204.8414 | 215 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 64 | 270 | 153 | 6 | 24 | 38 | 24 | 38 | 24 | 120
C | PSL-H2-R1 | 210.0081 | 220 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 64 | 270 | 153 | 6 | 24 | 38 | 24 | 38 | 24 | 38 | 24 | 120
C | SEI-H2-G3 | 215.5081 | 226 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 64 | 270 | 153 | 6 | 24 | 38 | 24 | 38 | 24 | 38 | 24 | 66 | 120
C | PSL-H2-T1 | 214.5789 | 225 | 7 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 396 | 64 | 270 | 115 | 231 | 48 | 59 | 96
C | SUS-H2-R2 | 122.354 | 132 | 5 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 51 | 10 | 32 | 120
C | WMCB3 ports | 116.2198 | 126 | 4 | 210 | 367 | 223 | 58 | 150 | 103 | 170 | 18 | 116.2389
C | WHAM9, port D1 | 107.0914 | 117 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 30 | 12 | 115 | 12 | 36
C | WHAM9, port D2 | 109.1748 | 119 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 30 | 12 | 115 | 12 | 33 | 28
C | WHAM9, port D3 | 112.5914 | 122 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 30 | 12 | 115 | 12 | 66 | 36
C | WHAM9, port D4 | 120.9248 | 130 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 30 | 12 | 115 | 12 | 100 | 66 | 36
C | WHAM9, port D5 | 117.5081 | 127 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 30 | 12 | 115 | 12 | 100 | 33 | 28
C | WHAM9, port D6 | 115.4248 | 125 | 6 | 210 | 367 | 223 | 58 | 150 | 103 | 30 | 12 | 115 | 12 | 100 | 36
C | WBSC4, far side, E & F ports | 99.4749 | 109 | 2 | 210 | 367 | 223 | 58 | 150 | 196
C | WBSC4, far side, G ports | 103.9624 | 113 | 3 | 210 | 367 | 223 | 58 | 150 | 196 | 59
C | WBSC7, far side, E & F ports | 121.5914 | 131 | 6 | 210 | 306 | 161 | 384 | 139 | 94 | 196
C | WBSC7, far side,G ports | 126.0789 | 136 | 7 | 210 | 306 | 161 | 384 | 139 | 94 | 196 | 59
C | SUS-H2-R5 | 104.2706 | 114 | 5 | 210 | 306 | 161 | 384 | 96 | 120
C | TCS-H2-R1 | 198.5538 | 208 | 9 | 210 | 306 | 161 | 384 | 139 | 94 | 100 | 28 | 32 | 807 | 24 | 24 | 120
C | TCS-H2-R2 | 70.4624 | 80 | 3 | 210 | 497 | 34 | 120
C | SUS-H2-R6 | 85.4499 | 95 | 4 | 210 | 306 | 161 | 249 | 120
C | SEI-H2-G3 | 115.6622 | 125 | 7 | 210 | 306 | 161 | 384 | 139 | 115 | 109
C | WBSC8, far side, E & F ports | 67.9749 | 77 | 2 | 210 | 319 | 43 | 58 | 196
C | WBSC8, far side, G ports | 72.4624 | 82 | 3 | 210 | 319 | 43 | 58 | 196 | 59
C | OPLEV-H2-Y1 | 92.1291 | 102 | 3 | 210 | 631 | 121 | 39 | 120
C | SUS-H2-R3 | 76.6291 | 86 | 3 | 210 | 367 | 206 | 32 | 120
C | WMCB4 ports | 81.8282 | 91 | 2 | 210 | 367 | 223 | 58 | 18 | 116.2389
C | WHAM10, port D1 | 94.5081 | 104 | 6 | 210 | 367 | 253 | 32 | 115 | 52 | 100 | 36
C | WHAM10, port D2 | 96.5914 | 106 | 6 | 210 | 367 | 253 | 32 | 115 | 52 | 100 | 33 | 28
C | WHAM10, port D3 | 100.0081 | 110 | 6 | 210 | 367 | 253 | 32 | 115 | 52 | 100 | 66 | 36
C | WHAM10, port D4 | 91.6748 | 101 | 6 | 210 | 367 | 253 | 32 | 115 | 52 | 66 | 36
C | WHAM10, port D5 | 88.2581 | 98 | 6 | 210 | 367 | 253 | 32 | 115 | 52 | 33 | 28
C | WHAM10, port D6 | 86.1748 | 96 | 6 | 210 | 367 | 253 | 32 | 115 | 52 | 36
C | TCS-H2-R3 | 71.9624 | 81 | 3 | 210 | 367 | 182 | 120
C | TCS-H2-XC | 17.5 | 27 |  | 210
C | TCS-H2-YC | 17.5 | 27 |  | 210
C | WMCA4 ports | 78.9115 | 88 | 2 | 210 | 367 | 166 | 50 | 30 | 18 | 116.2389
C | WHAM11, port D1 | 80.854 | 90 | 5 | 210 | 367 | 207 | 115 | 61 | 36
C | WHAM11, port D2 | 82.9373 | 92 | 5 | 210 | 367 | 207 | 115 | 61 | 33 | 28
C | WHAM11, port D3 | 86.354 | 96 | 5 | 210 | 367 | 207 | 115 | 61 | 66 | 36
C | WHAM11, port D4 | 94.6873 | 104 | 5 | 210 | 367 | 207 | 115 | 61 | 100 | 66 | 36
C | WHAM11, port D5 | 91.2706 | 101 | 5 | 210 | 367 | 207 | 115 | 61 | 100 | 33 | 28
C | WHAM11, port D6 | 89.1873 | 99 | 5 | 210 | 367 | 207 | 115 | 61 | 100 | 36
C | WHAM12, port D1 | 89.1873 | 99 | 5 | 210 | 367 | 207 | 115 | 61 | 100 | 36
C | WHAM12, port D2 | 91.2706 | 101 | 5 | 210 | 367 | 207 | 115 | 61 | 100 | 33 | 28
C | WHAM12, port D3 | 94.6873 | 104 | 5 | 210 | 367 | 207 | 115 | 61 | 100 | 66 | 36
C | WHAM12, port D4 | 103.0206 | 113 | 5 | 210 | 367 | 207 | 115 | 61 | 200 | 66 | 36
C | WHAM12, port D5 | 99.604 | 109 | 5 | 210 | 367 | 207 | 115 | 61 | 200 | 33 | 28
C | WHAM12, port D6 | 97.5206 | 107 | 5 | 210 | 367 | 207 | 115 | 61 | 200 | 36
C | ISC-H2-R3 | 103.6416 | 113 | 2 | 210 | 367 | 166 | 50 | 341 | 120
C | SUS-H2-R4 | 105.8916 | 115 | 2 | 210 | 367 | 166 | 50 | 368 | 120
C | SEI-GND-H2-2 | 109.9749 | 119 | 2 | 210 | 367 | 166 | 50 | 417 | 120
C | OPLEV-H2-X1 | 222.3038 | 233 | 9 | 210 | 306 | 161 | 384 | 139 | 94 | 100 | 28 | 32 | 993 | 107 | 40 | 120

## H2 - pt C to Rack Room
H2 - POINT C TO RACK ROOM |  |  |  | length margin = | 5% | or | 120 | inches, whichever is longer
|  | LENGTH (ft) |  | bend radius = | 12
POINT | RACK | BASIC | with margin | # 90 deg BENDS | intermediate lengths in inches:
C | H2-PSL-C1 | 32.1667 | 42 |  | 135 | 119 | 12 | 120
C | H2-UNK-C4 | 34.1667 | 44 |  | 135 | 119 | 12 | 24 | 120
C | H2-UNK-C5 | 36.1667 | 46 |  | 135 | 119 | 12 | 24 | 24 | 120
C | H2-AOS-C1 | 38.1667 | 48 |  | 135 | 119 | 12 | 24 | 24 | 24 | 120
C | H2-SEI-C1 | 43.1667 | 53 |  | 135 | 119 | 144 | 120
C | H2-SEI-C2 | 45.1667 | 55 |  | 135 | 119 | 144 | 24 | 120
C | H2-SEI-C3 | 47.1667 | 57 |  | 135 | 119 | 144 | 24 | 24 | 120
C | H2-SEI-C4 | 49.1667 | 59 |  | 135 | 119 | 144 | 24 | 24 | 24 | 120
C | H2-SEI-C5 | 51.1667 | 61 |  | 135 | 119 | 144 | 24 | 24 | 24 | 24 | 120
C | H2-SEI-C6 | 53.1667 | 63 |  | 135 | 119 | 144 | 24 | 24 | 24 | 24 | 24 | 120
C | H2-SUS-C4 | 25.25 | 35 |  | 135 | 24 | 24 | 120
C | H2-SUS-C3 | 23.25 | 33 |  | 135 | 24 | 120
C | H2-SUS-C2 | 21.25 | 31 |  | 135 | 120
C | H2-SUS-C1 | 23.25 | 33 |  | 135 | 24 | 120
C | H2-SUS-C5 | 33.3333 | 43 |  | 135 | 97 | 24 | 24 | 120
C | H2-SUS-C6 | 31.3333 | 41 |  | 135 | 97 | 24 | 120
C | H2-SUS-C7 | 29.3333 | 39 |  | 135 | 97 | 120
C | H2-SUS-C8 | 31.3333 | 41 |  | 135 | 97 | 24 | 120
C | H2-PEM-C1 | 39.6667 | 49 |  | 135 | 97 | 76 | 24 | 24 | 120
C | H2-UNK-C3 | 37.6667 | 47 |  | 135 | 97 | 76 | 24 | 120
C | H2-UNK-C2 | 35.6667 | 45 |  | 135 | 97 | 76 | 120
C | H2-UNK-C1 | 37.6667 | 47 |  | 135 | 97 | 76 | 24 | 120
C | H2-ISC-C1 | 47.25 | 57 |  | 135 | 97 | 76 | 91 | 24 | 24 | 120
C | H2-ISC-C2 | 45.25 | 55 |  | 135 | 97 | 76 | 91 | 24 | 120
C | H2-ISC-C3 | 43.25 | 53 |  | 135 | 97 | 76 | 91 | 120
C | H2-VDC-C1 | 73.3333 | 83 |  | 135 | 119 | 482 | 24 | 120
C | H2-VDC-C2 | 75.3333 | 85 |  | 135 | 119 | 482 | 24 | 24 | 120
C | H2-VDC-C3 | 77.3333 | 87 |  | 135 | 119 | 482 | 24 | 24 | 24 | 120
C | H2-VDC-C4 | 79.3333 | 89 |  | 135 | 119 | 482 | 24 | 24 | 24 | 24 | 120

## H2 - LVEA rack to chamber
H2 - LVEA RACK TO CHAMBER/TABLE |  |  |  | length margin = | 5% | or | 120 | inches, whichever is longer
|  | LENGTH (ft) |  | bend radius = | 12
RACK | CHAMBER/TABLE | BASIC | with margin | # 90 deg BENDS | intermediate lengths in inches:
ISC-H2-R1 | H2-ISCHT7L | 30.6999 | 40 | 4 | 120 | 24 | 38 | 24 | 12 | 38 | 49 | 84
ISC-H2-R1 | WHAM7, port D1 | 50.5206 | 60 | 5 | 120 | 24 | 38 | 24 | 12 | 96 | 115 | 67 | 100 | 36
ISC-H2-R1 | WHAM7, port D2 | 52.604 | 62 | 5 | 120 | 24 | 38 | 24 | 12 | 96 | 115 | 67 | 100 | 33 | 28
ISC-H2-R1 | WHAM7, port D3 | 56.0206 | 66 | 5 | 120 | 24 | 38 | 24 | 12 | 96 | 115 | 67 | 100 | 66 | 36
ISC-H2-R1 | WHAM7, port D4 | 47.6873 | 57 | 5 | 120 | 24 | 38 | 24 | 12 | 96 | 115 | 67 | 66 | 36
ISC-H2-R1 | WHAM7, port D5 | 44.2706 | 54 | 5 | 120 | 24 | 38 | 24 | 12 | 96 | 115 | 67 | 33 | 28
ISC-H2-R1 | WHAM7, port D6 | 42.1873 | 52 | 5 | 120 | 24 | 38 | 24 | 12 | 96 | 115 | 67 | 36
ISC-H2-R2 | H2-ISCHT7L | 25.5332 | 35 | 4 | 120 | 24 | 12 | 38 | 49 | 84
ISC-H2-R2 | WHAM7, port D1 | 45.354 | 55 | 5 | 120 | 24 | 12 | 96 | 115 | 67 | 100 | 36
ISC-H2-R2 | WHAM7, port D2 | 47.4373 | 57 | 5 | 120 | 24 | 12 | 96 | 115 | 67 | 100 | 33 | 28
ISC-H2-R2 | WHAM7, port D3 | 50.854 | 60 | 5 | 120 | 24 | 12 | 96 | 115 | 67 | 100 | 66 | 36
ISC-H2-R2 | WHAM7, port D4 | 42.5206 | 52 | 5 | 120 | 24 | 12 | 96 | 115 | 67 | 66 | 36
ISC-H2-R2 | WHAM7, port D5 | 39.104 | 49 | 5 | 120 | 24 | 12 | 96 | 115 | 67 | 33 | 28
ISC-H2-R2 | WHAM7, port D6 | 37.0206 | 47 | 5 | 120 | 24 | 12 | 96 | 115 | 67 | 36
SUS-H2-R1 | WHAM8, port D1 | 31.3665 | 41 | 4 | 120 | 24 | 50 | 115 | 52 | 36
SUS-H2-R1 | WHAM8, port D2 | 33.4499 | 43 | 4 | 120 | 24 | 50 | 115 | 52 | 33 | 28
SUS-H2-R1 | WHAM8, port D3 | 36.8665 | 46 | 4 | 120 | 24 | 50 | 115 | 52 | 66 | 36
SUS-H2-R1 | WHAM8, port D4 | 45.1999 | 55 | 4 | 120 | 24 | 50 | 115 | 52 | 100 | 66 | 36
SUS-H2-R1 | WHAM8, port D5 | 41.7832 | 51 | 4 | 120 | 24 | 50 | 115 | 52 | 100 | 33 | 28
SUS-H2-R1 | WHAM8, port D6 | 39.6999 | 49 | 4 | 120 | 24 | 50 | 115 | 52 | 100 | 36
SUS-H2-R2 | WHAM9, port D1 | 41.1999 | 51 | 4 | 120 | 24 | 24 | 40 | 115 | 56 | 100 | 36
SUS-H2-R2 | WHAM9, port D2 | 43.2832 | 53 | 4 | 120 | 24 | 24 | 40 | 115 | 56 | 100 | 33 | 28
SUS-H2-R2 | WHAM9, port D3 | 46.6999 | 56 | 4 | 120 | 24 | 24 | 40 | 115 | 56 | 100 | 66 | 36
SUS-H2-R2 | WHAM9, port D4 | 38.3665 | 48 | 4 | 120 | 24 | 24 | 40 | 115 | 56 | 66 | 36
SUS-H2-R2 | WHAM9, port D5 | 34.9499 | 44 | 4 | 120 | 24 | 24 | 40 | 115 | 56 | 33 | 28
SUS-H2-R2 | WHAM9, port D6 | 32.8665 | 42 | 4 | 120 | 24 | 24 | 40 | 115 | 56 | 36
TCS-H2-R1 | H2-TCSX | 30.4499 | 40 | 4 | 120 | 33 | 115 | 70 | 48
SUS-H2-R3 | WHAM10, port D1 | 40.4499 | 50 | 4 | 120 | 12 | 24 | 47 | 115 | 52 | 100 | 36
SUS-H2-R3 | WHAM10, port D2 | 42.5332 | 52 | 4 | 120 | 12 | 24 | 47 | 115 | 52 | 100 | 33 | 28
SUS-H2-R3 | WHAM10, port D3 | 45.9499 | 55 | 4 | 120 | 12 | 24 | 47 | 115 | 52 | 100 | 66 | 36
SUS-H2-R3 | WHAM10, port D4 | 37.6165 | 47 | 4 | 120 | 12 | 24 | 47 | 115 | 52 | 66 | 36
SUS-H2-R3 | WHAM10, port D5 | 34.1999 | 44 | 4 | 120 | 12 | 24 | 47 | 115 | 52 | 33 | 28
SUS-H2-R3 | WHAM10, port D6 | 32.1165 | 42 | 4 | 120 | 12 | 24 | 47 | 115 | 52 | 36
TCS-H2-R3 | H2-TCSHT10 | 33.3289 | 43 | 7 | 120 | 27 | 75 | 27 | 115 | 24 | 48
ISC-H2-R3 | H2-ISCHT12R | 35.7832 | 45 | 4 | 120 | 45 | 160 | 41 | 84
ISC-H2-R3 | WHAM12, port D1 | 36.3665 | 46 | 4 | 120 | 45 | 115 | 41 | 100 | 36
ISC-H2-R3 | WHAM12, port D2 | 38.4499 | 48 | 4 | 120 | 45 | 115 | 41 | 100 | 33 | 28
ISC-H2-R3 | WHAM12, port D3 | 41.8665 | 51 | 4 | 120 | 45 | 115 | 41 | 100 | 66 | 36
ISC-H2-R3 | WHAM12, port D4 | 33.5332 | 43 | 4 | 120 | 45 | 115 | 41 | 66 | 36
ISC-H2-R3 | WHAM12, port D5 | 30.1165 | 40 | 4 | 120 | 45 | 115 | 41 | 33 | 28
ISC-H2-R3 | WHAM12, port D6 | 28.0332 | 38 | 4 | 120 | 45 | 115 | 41 | 36
SUS-H2-R4 | WHAM11, port D1 | 46.9499 | 56 | 4 | 120 | 72 | 115 | 41 | 200 | 36
SUS-H2-R4 | WHAM11, port D2 | 49.0332 | 59 | 4 | 120 | 72 | 115 | 41 | 200 | 33 | 28
SUS-H2-R4 | WHAM11, port D3 | 52.4499 | 62 | 4 | 120 | 72 | 115 | 41 | 200 | 66 | 36
SUS-H2-R4 | WHAM11, port D4 | 44.1165 | 54 | 4 | 120 | 72 | 115 | 41 | 100 | 66 | 36
SUS-H2-R4 | WHAM11, port D5 | 40.6999 | 50 | 4 | 120 | 72 | 115 | 41 | 100 | 33 | 28
SUS-H2-R4 | WHAM11, port D6 | 38.6165 | 48 | 4 | 120 | 72 | 115 | 41 | 100 | 36
SUS-H2-R4 | WHAM12, port D1 | 38.6165 | 48 | 4 | 120 | 72 | 115 | 41 | 100 | 36
SUS-H2-R4 | WHAM12, port D2 | 40.6999 | 50 | 4 | 120 | 72 | 115 | 41 | 100 | 33 | 28
SUS-H2-R4 | WHAM12, port D3 | 44.1165 | 54 | 4 | 120 | 72 | 115 | 41 | 100 | 66 | 36
SUS-H2-R4 | WHAM12, port D4 | 35.7832 | 45 | 4 | 120 | 72 | 115 | 41 | 66 | 36
SUS-H2-R4 | WHAM12, port D5 | 32.3665 | 42 | 4 | 120 | 72 | 115 | 41 | 33 | 28
SUS-H2-R4 | WHAM12, port D6 | 30.2832 | 40 | 4 | 120 | 72 | 115 | 41 | 36
SUS-H2-R5 | WBSC4, far side, E & F ports | 52.0623 | 62 | 4 | 120 | 96 | 189 | 44 | 196.3495
SUS-H2-R5 | WBSC7, far side, E & F ports | 40.3249 | 50 | 3 | 120 | 65 | 24 | 94 | 196.3495
SUS-H2-R6 | WBSC8, far side, E & F ports | 68.3956 | 78 | 4 | 120 | 249 | 161 | 14 | 43 | 58 | 196.3495
SUS-H2-R6 | WBSC4, far side, E & F ports | 41.4082 | 51 | 3 | 120 | 98 | 98 | 196.3495
TCS-H2-R2 | H2-TCSY | 20.9749 | 30 | 2 | 120 | 24 | 70 | 48

## tray sizing
TRAY SIZING
| dia (in) | 0.637 | 0.514 | 0.411 | 0.375
Tray | # conductors | 25 pin | 15 pin | 9 pin | 3 pin | Area (in^2) | height | width
|  | 164 | 61 | 24 | 61 | 299.3759 | 12 | 24.948
|  | 33 | 17 | 8 | 30 | 73.6761 | 12 | 6.1397
|  | 23 | 26 | 8 | 8 | 58.6791 | 5 | 11.7358
|  | 99 | 26 | 8 | 8 | 155.561 | 6 | 25.9268
|  | 111 | 0 | 0 | 0 | 141.4985 | 6 | 23.5831
|  | 20 | 7 | 4 | 15 | 40.0547 | 6 | 6.6758
|  | 45 | 28 | 12 | 38 | 103.7602 | 6 | 17.2934
incomplete!