LIGO Laboratory / LIGO Scientific Collaboration

LIGO-T070256-00-D	LIGO	Date:  10/16/2007

Beam Tube and Enclosure Inspection

Allen Sibley

Distribution of this document:

LIGO Science Collaboration

This is an internal working note

of the LIGO Project.

| California Institute of Technology LIGO Project – MS 18-34 1200 E. California Blvd. Pasadena, CA 91125 Phone (626) 395-2129 Fax (626) 304-9834 E-mail: info@ligo.caltech.edu | Massachusetts Institute of Technology LIGO Project – NW17-161 175 Albany St Cambridge, MA 02139 Phone (617) 253-4824 Fax (617) 253-7014 E-mail: info@ligo.mit.edu |
| --- | --- |
| LIGO Hanford Observatory P.O. Box 1970 Mail Stop S9-02 Richland WA 99352 Phone 509-372-8106 Fax 509-372-8137 | LIGO Livingston Observatory P.O. Box 940 Livingston, LA 70754 Phone 225-686-3100 Fax 225-686-7189 |

http://www.ligo.caltech.edu/

# Introduction

Beam tube and enclosure should be inspected inside and outside, including the backside, every three years. Personnel familiar with the beam tubes and enclosure construction should conduct the inspection.

# Inspection

Before inspection provide for the following:

1.  	Open doors of section to be inspected 24 hrs before entry and ventilate with fans.

- Inspection team must be properly suited for entry.

- Provide adequate lighting for safety and ease of inspection.

The following areas should be noted during inspection along with any unusual conditions:

- Condition and security of the insulation blankets. Is vapor barrier in place?

- Fixed tube supports, any sign of excessive rust or corrosion?

- Guide supports, any sign of wire cable abrading or corrosion?

- Pump port hardware, is the gate valve in good condition and is insect guard in place and hole free? Do Not Operate Valve! Is all other hardware in good condition?

- General condition of the concrete enclosure. Is grout and caulking in good condition?

- Check electrical ground are connected.

## An inspection of the tube surface should be done in several random places by removing the insulation and with good lighting inspect the steel, especially at the weld for any sign of corrosion, rusting or other conditions. Insulation should be replaced and taped as necessary. Any defects or deficiencies are that cannot be repaired during inspection should be noted in a log along with its location relative to the nearest door.