## Slide 1: EtherCAT (Beckhoff) for advanced LIGO
January 25, 2011
CDS Meeting, LHO
ISC Implementation

## Slide 2: Why?
Need to replace VME based EPICS system
Used in the aLIGO PSL
  Don’t want to maintain more systems than necessary
  Used in the squeezer for slow controls
Good enough
  100base Ethernet (no expensive backbone)
  Low latency: Datagrams processed on the fly
  Fast: 1-10 ms readout standard; 100us possible
  Software: Windows based with EPICS interface
  Modern
Cost effective for large number of slow channels
  Stackable, DIN-rail mounted units with 1-4 channels typical
  16 bit analog channel: ~$50-$100
  Binary channel: ~$10-$20

## Slide 3: What is EtherCAT?

## Slide 4: What is EtherCAT?
Protocol: (Raw) Ethernet frames
  Memory mapped access (4GB)
  UDP/IP encapsulation possible
Performance
  Real-time kernel on PC
  1000 distributed I/Os in only 30 µs
Topology
  Line, star or tree; hot connect of branches possible
  up to 65,535 devices
  E-bus (LVDS) for DIN mounted modules
  Stand-alone modules (IP67)
Distributed Clock
Special Safety Terminal
Useful information video

## Slide 5: EtherCAT Coupler
Ethernet
NEXT
IN
E-Bus
Power
E-Bus:
– Ethernet OUT (LVDS)
– Ethernet IN (LVDS)
– 5V Power
Power:
– Positive (24V/5V)
– Ground
– Shield
DIN rail
Coupler requires +24V
to power E-Bus
Separate power for terminals

## Slide 6: EtherCAT Terminal
4-channel binary TTL output
2-channel 16-bit analog input

## Slide 7: 3U Chassis Design

## Slide 8: 3U Chassis Design

## Slide 9: 3U Chassis Features
EtherCAT connections
  2 front panel 100baseFX (fiber) input/output connections
  2 auxiliary rear panel 100baseT connections (optional)
Power
  24 VDC/5 A max (digital); 3-pin power D-sub
  On-Off Switch/thermal breaker
  Internal DC-DC converters for 5 VDC
9 rear adapter slots
  1x 37pin/25pin D-sub
  2x 15pin/9pin D-sub
  Others…
3 internal DIN rails (20”)

## Slide 10: Ethernet Configuration
Fiber IN
Fiber OUT
Aux 1
Aux 2
Unconnected ports are automatically closed

## Slide 11: Power and Grounding (1)
Analog terminals 1
  Differential 16 bit analog inputs: EL3101 (1 chn), EL3102 (2 chn)
  Differential 16 bit analog outputs: EL4132 (2 chn)
  No connection to power bus
  Common needs to be connected to
    Signal ground of controlled chassis (preferred), or
    Local power ground
Analog terminals 2
  4 channel terminals: EL3104 and EL4134
  Common connected to power bus ground
  Connect power bus ground to signal or local power ground
  May require feed terminal EL9190 to break power bus

## Slide 12: Power and Grounding (2)
Binary terminals
  TTL input : EL1124 (4 chn)
  TTL output: EL2124 (4 chn)
  TTL ground connected to power bus ground
    Connect power bus ground to digital ground of controlled chassis
  Powered from power bus: 5 VDC
    Requires isolated DC-DC converter 24V in/5V out
  Typically requires feed terminal EL9190 to break power bus and supply 5 VDC
Other terminals
  EL9400: Power supply for E-Bus
  EK1110/EL9011: Extension end terminal/End cap
  EL6002/EL6022: Dual RS232/RS422 interface

## Slide 13: Programmable Logic Controller (PLC)
Computer room:
Supermicro 2U(?)
Software:
TwinCAT PLC
Controller Toolbox
Serial Communications
OPC Server
EPICS Interface
FC9022 (dual chn NIC)
EtherCAT chassis (optional)
– Fiber converter
– Weather stations, etc.
– Time Synchronization
Fiber to
Electronics room
Spare
1 Computer per station and interferometer

## Slide 14: Software
Real-time task
EtherCAT
Process variables
Shared Memory
Periodic
User task
Periodic
User task
OPC Server
EPICS Interface
EPICS
Local user screen

## Slide 15: Outlook
Easy to expand; easy to add a few more channels
Simple logic controllers and slow servos can be directly implemented in the Beckhoff PLC
TwinCAT 3 will support 64bit OS and C++/Matlab
We can support RS232/RS422/RS485 devices
Infrastructure to support legacy and “odd-ball” devices (picomotors, dust monitors, rotating waveplates, weather stations, etc.)
Future of the vacuum controls?