## Corner Left
MSR Chassis Corner |  | Left Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | L | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | L | EK1101 | 0 | 0V | P | TBLOCK
24V | violet | L | EK1101 | 0 | + | P | TBLOCK
0V | gray | L | EK1101 | 0 | – | P | TBLOCK
24V | violet | L | EL9400 | 7 | 24V | P | TBLOCK
0V | gray | L | EL9400 | 7 | 0V | P | TBLOCK
24V | violet | L | EL9400 | 7 | + | P | TBLOCK
0V | gray | L | EL9400 | 7 | – | P | TBLOCK
Communication
EtherCAT in | CAT5 | L | EK1101 | 0 | X1 | Comm. | Front | In
EtherCAT out | CAT5 | L | EK1101 | 0 | X2 | Comm. | Front | Out
Temperature
Temperature Supply 1 + | red | L | EL3202 | 2 | +R1 | AI | 6 | 1-2
Temperature Supply 1 – | black | L | EL3102 | 2 | –R1 | AI | 6 | 1-4
Temperature Readback 1 + | green | L | EL3102 | 2 | +R1 | AI | 6 | 1-1
Temperature Readback 1 – | white | L | EL3102 | 2 | –R1 | AI | 6 | 1-3
Temperature Supply 2 + | red | L | EL3202 | 2 | +R2 | AI | 6 | 2-2
Temperature Supply 2 – | black | L | EL3102 | 2 | –R2 | AI | 6 | 2-4
Temperature Readback 2 + | green | L | EL3102 | 2 | +R2 | AI | 6 | 2-1
Temperature Readback 2 – | white | L | EL3102 | 2 | –R2 | AI | 6 | 2-3
Communication
PTP | CAT5 | L | EL6688 | 3 | X1 | Comm. | Rear port | 2
Serial
Weather station | D-sub | L | EL6002 | 5 | X1 | Serial | 7 | 1
Timing GPS | D-sub | L | EL6002 | 5 | X2 | Serial | 7 | 2
Spare RS232 | D-sub | L | EL6002 | 8 | X1 | Serial | 7 | 3
Fiber polarization control | D-sub | L | EL6002 | 8 | X2 | Serial | 7 | 4
Spare RS422 | D-sub | L | EL6022 | 10 | X1 | Serial | 7 | 7
Timing master fanout | D-sub | L | EL6022 | 10 | X2 | Serial | 7 | 8
Temperature terminals are coded red and blue for the supply lines and yellow for the readback lines.

## Corner Middle
MSR Chassis Corner |  | Middle Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
empty

## Corner Right
MSR Chassis Corner |  | Right Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
empty

## End Left
Remote Access Chassis End |  | Left Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | L | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | L | EK1101 | 0 | 0V | P | TBLOCK
24V | violet | L | EK1101 | 0 | + | P | TBLOCK
0V | gray | L | EK1101 | 0 | – | P | TBLOCK
Communication
Corner EtherCAT in | SM fiber | L | EK1501 | 0 | X1 | Comm. | Front | In
Corner EtherCAT out | SM fiber | L | EK1501 | 0 | X2 | Comm. | Front | Out
MM fiber end | MM fiber | L | EK1521 | 2 | X1 | Comm. | Rear port | 1
Temperature
Temperature Supply 1 + | red | L | EL3202 | 1 | +R1 | AI | 6 | 1-2
Temperature Supply 1 – | black | L | EL3102 | 1 | –R1 | AI | 6 | 1-4
Temperature Readback 1 + | green | L | EL3102 | 1 | +R1 | AI | 6 | 1-1
Temperature Readback 1 – | white | L | EL3102 | 1 | –R1 | AI | 6 | 1-3
Temperature Supply 2 + | red | L | EL3202 | 1 | +R2 | AI | 6 | 2-2
Temperature Supply 2 – | black | L | EL3102 | 1 | –R2 | AI | 6 | 2-4
Temperature Readback 2 + | green | L | EL3102 | 1 | +R2 | AI | 6 | 2-1
Temperature Readback 2 – | white | L | EL3102 | 1 | –R2 | AI | 6 | 2-3
Communication
MM fiber end | MM fiber | L | EK1521 | 2 | X1 | Comm. | Rear port | 1
Serial
H0 weather | D-sub | L | EL6002 | 4 | X1 | Serial | 7 | 1
H0 GPS 1 | D-sub | L | EL6002 | 4 | X2 | Serial | 7 | 2
Spare RS422 | D-sub | L | EL6022 | 6 | X1 | Serial | 7 | 7
H0 timing master | D-sub | L | EL6022 | 6 | X2 | Serial | 7 | 8
Communication
EtherCAT out | CAT5 | L | EK1101 | 8 | X2 | Comm. | L/GW_1 | X1.1
X-Gateway Modbus
Output | CAT5 | L | AB9000 | GW_1 | X1.2 | Comm. | Rear port | 2
Modbus 1 | CAT5 | L | AB9000 | GW_1 | X2.1 | Comm. | 7 | 1
Modbus 2 | CAT5 | L | AB9000 | GW_1 | X2.2 | Comm. | 7 | 2
Temperature terminals are coded red and blue for the supply lines and yellow for the readback lines.

## End Middle
Remote Access Chassis End |  | Middle Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
empty

## End Right
Remote Access Chassis End |  | Right Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
empty