## Chassis PSL Left
PSL Chassis |  | Left Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | L | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | L | EK1101 | 0 | 0V | P | TBLOCK
24V | violet | L | EK1101 | 0 | + | P | TBLOCK | +V
0V | gray | L | EK1101 | 0 | – | P | TBLOCK | –V
24V | violet |  | TBLOCK |  | 24V | P | 5 | P7
0V | gray |  | TBLOCK |  | 0V | P | 5 | P8
24V | violet |  | TBLOCK |  | 24V | P | 6 | P7
0V | gray |  | TBLOCK |  | 0V | P | 6 | P8
24V | violet |  | TBLOCK |  | 24V | P | 7 | P7
0V | gray |  | TBLOCK |  | 0V | P | 7 | P8
24V | violet |  | TBLOCK |  | 24V | P | 8 | P7
0V | gray |  | TBLOCK |  | 0V | P | 8 | P8
Coupler
Input | CAT5 | L | EK1101 | 0 | X1 | Comm. | IN
Output | CAT5 | L | EK1101 | 0 | X2 | Comm. | R/0 | X1
Rotation Stages
Encoder A: A (IO) | brown | L | EL7342 | 1 | A/top | BI | 8 | P4
Encoder A: B (IO) | brown | L | EL7342 | 1 | B/top | BI | 8 | P5
Encoder B: A (Spare) | brown | L | EL7342 | 1 | A/below | BI | 5 | P4
Encoder B: B (Spare) | brown | L | EL7342 | 1 | B/below | BI | 5 | P5
Input A (IO) | brown | L | EL7342 | 1 | I1 | BI | 8 | P3
Input B (Spare) | brown | L | EL7342 | 1 | I2 | BI | 5 | P3
Motor A1(*) (IO) | violet | L | EL7342 | 2 | A1 | P | 8 | PWR/S
Motor A2(*) (IO) | gray | L | EL7342 | 2 | A2 | P | 8 | PWR/P
Motor B1(*) (Spare) | violet | L | EL7342 | 2 | B1 | P | 5 | PWR/S
Motor B2(*) (Spare) | gray | L | EL7342 | 2 | B2 | P | 5 | PWR/P
24V(*) | violet | L | EL7342 | 2 | + | P | L/4 | +
0V(*) | gray | L | EL7342 | 2 | – | P | L/4 | –
Encoder A: A (TCSX) | brown | L | EL7342 | 3 | A/top | BI | 6 | P4
Encoder A: B (TCSX) | brown | L | EL7342 | 3 | B/top | BI | 6 | P5
Encoder B: A (TCSY) | brown | L | EL7342 | 3 | A/below | BI | 7 | P4
Encoder B: B (TCSY) | brown | L | EL7342 | 3 | B/below | BI | 7 | P5
Input A (TCSX) | brown | L | EL7342 | 3 | I1 | BI | 6 | P3
Input B (TCSY) | brown | L | EL7342 | 3 | I2 | BI | 7 | P3
Motor A1(*) (TCSX) | violet | L | EL7342 | 4 | A1 | P | 6 | PWR/S
Motor A2(*) (TCSX) | gray | L | EL7342 | 4 | A2 | P | 6 | PWR/P
Motor B1(*) (TCSY) | violet | L | EL7342 | 4 | B1 | P | 7 | PWR/S
Motor B2(*) (TCSY) | gray | L | EL7342 | 4 | B2 | P | 7 | PWR/P
24V(*)(**) | violet | L | EL7342 | 4 | + | P | TBLOCK
0V(*)(**) | gray | L | EL7342 | 4 | – | P | TBLOCK
Interlock Mon (IO) | brown | L | EL1094 | 5 | I1 | BI | 8 | P9
Interlock Mon (Spare) | brown | L | EL1094 | 5 | I2 | BI | 5 | P9
Interlock Mon (TCSX) | brown | L | EL1094 | 5 | I3 | BI | 6 | P9
Interlock Mon (TCSY) | brown | L | EL1094 | 5 | I4 | BI | 7 | P9
IO PZTs
Return | black | L | EL9190 | 6 | – | P | 9 | 1/8
V-Mon 1 + | green | L | EL3104 | 7 | +I1 | AI | 9 | 1/3
V-Mon 1 – | white | L | EL3104 | 7 | –I1 | AI | L/6 | Return
V-Mon 2 + | green | L | EL3104 | 7 | +I2 | AI | 9 | 1/4
V-Mon 2 – | white | L | EL3104 | 7 | –I2 | AI | L/6 | Return
SGS-Mon X + | green | L | EL3104 | 7 | +I3 | AI | 9 | 1/9
SGS-Mon X – | white | L | EL3104 | 7 | –I3 | AI | L/6 | Return
SGS-Mon Y + | green | L | EL3104 | 7 | +I4 | AI | 9 | 1/10
SGS-Mon Y – | white | L | EL3104 | 7 | –I4 | AI | L/6 | Return
Return | black | L | EL9190 | 8 | – | P | 9 | 2/8
V-Mon 1 + | green | L | EL3104 | 9 | +I1 | AI | 9 | 2/3
V-Mon 1 – | white | L | EL3104 | 9 | –I1 | AI | L/8 | Return
V-Mon 2 + | green | L | EL3104 | 9 | +I2 | AI | 9 | 2/4
V-Mon 2 – | white | L | EL3104 | 9 | –I2 | AI | L/8 | Return
SGS-Mon X + | green | L | EL3104 | 9 | +I3 | AI | 9 | 2/9
SGS-Mon X – | white | L | EL3104 | 9 | –I3 | AI | L/8 | Return
SGS-Mon Y + | green | L | EL3104 | 9 | +I4 | AI | 9 | 2/10
SGS-Mon Y – | white | L | EL3104 | 9 | –I4 | AI | L/8 | Return
(*) AWG16, twist pairs
(**) Wrap twisted pair through a common mode choke, 10 turns, then connect to terminal block

## Chassis PSL Right
PSL Chassis |  | Right Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24VInput | violet | R | EK1501 | 0 | 24V | P | TBLOCK
0VInput | gray | R | EK1501 | 0 | 0V | P | TBLOCK
24VInput | violet | R | EK1501 | 0 | + | P | TBLOCK
0VInput | gray | R | EK1501 | 0 | – | P | TBLOCK
Coupler
Output | CAT5 | R | EK1100 | 0 | X2 | Comm. | OUT
Environmental
H1:PSL-ENV_LASERRM_ACSTEMP(+V)out | violet | R | EL3154 | 1 | 24V | P | 1 | 1
H1:PSL-ENV_LASERRM_ACSTEMP(current)in | green | R | EL3154 | 1 | I1 | AI | 1 | 14
H1:PSL-ENV_LASERRM_ACNTEMP(+V)out | violet | R | EL3154 | 1 | 24V | P | 1 | 2
H1:PSL-ENV_LASERRM_ACNTEMP(current)in | green | R | EL3154 | 1 | I2 | AI | 1 | 15
H1:PSL-ENV_LASERRM_TBLNTEMP(+V)out | violet | R | EL3154 | 1 | 24V | P | 1 | 3
H1:PSL-ENV_LASERRM_TBLNTEMP(current)in | green | R | EL3154 | 1 | I3 | AI | 1 | 16
H1:PSL-ENV_LASERRM_RH(current)in | green | R | EL3154 | 1 | I4 | AI | 1 | 4
H1:PSL-ENV_LASERRM_TBLSTEMP(+V)out | violet | R | EL3154 | 2 | 24V | P | 1 | 5
H1:PSL-ENV_LASERRM_TBLSTEMP(current)in | green | R | EL3154 | 2 | I1 | AI | 1 | 18
H1:PSL-ENV_ANTERM_TEMP(+V)out | violet | R | EL3154 | 2 | 24V | P | 1 | 6
H1:PSL-ENV_ANTERM_TEMP(current)in | green | R | EL3154 | 2 | I2 | AI | 1 | 19
H1:PSL-ENV_ANTERM_RH(current)in | green | R | EL3154 | 2 | I3 | AI | 1 | 7
H1:PSL-ENV_LVEA_TEMP(+V)out | violet | R | EL3154 | 2 | 24V | P | 1 | 8
H1:PSL-ENV_LVEA_TEMP(current)in | green | R | EL3154 | 2 | I4 | Al | 1 | 21
H1:PSL-ENV_LASERRMTOANTERM_DPRES(+V)out | violet | R | EL3154 | 3 | 24v | P | 1 | 9
H1:PSL-ENV_LASERRMTOANTERM_DPRES(current)in | green | R | EL3154 | 3 | I1 | AI | 1 | 22
H1:PSL-ENV_ANTERMTOLVEA_DPRES(+V)out | violet | R | EL3154 | 3 | 24V | P | 1 | 10
H1:PSL-ENV_ANTERMTOLVEA_DPRES(current)in | green | R | EL3154 | 3 | I2 | AI | 1 | 23
H1:PSL-ENV_DIODERM_TEMP(+V)out | violet | R | EL3154 | 3 | 24V | P | 2 | 1
H1:PSL-ENV_DIODERM_TEMP(current)in | green | R | EL3154 | 3 | I3 | AI | 2 | 14
H1:PSL-ENV_DIODERM_RH(current)in | green | R | EL3154 | 3 | I4 | AI | 2 | 2
H1:PSL-ENV_CHILLERRM_TEMP(+V)out | violet | R | EL3154 | 4 | 24V | P | 2 | 3
H1:PSL-ENV_CHILLERRM_TEMP(current)in | green | R | EL3154 | 4 | I1 | AI | 2 | 16
H1:PSL-ENV_CHILLERRM_RH(current)in | green | R | EL3154 | 4 | I2 | AI | 2 | 4
H1:PSL-ENV_DIODERMTOCHILLERRM_DPRES(+V)out | violet | R | EL3154 | 4 | 24V | P | 2 | 5
H1:PSL-ENV_DIODERMTOCHILLERRM_DPRES(current)in | green | R | EL3154 | 4 | I3 | AI | 2 | 18
(Empty) | violet | R | EL3154 | 4 | 24V | P | 2 | 6
(Empty) | green | R | EL3154 | 4 | I4 | AI | 2 | 19