## Chassis End 2 Left
End Station Controls Chassis 2 |  | Left Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | L | OMRON | DC_1 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_1 | 0V | P | TBLOCK
24V | violet | L | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | L | EK1101 | 0 | 0V | P | TBLOCK
5V_1 | red | L | EK1101 | 0 | + | P | DC_1 | +V
5VRET_1 | black | L | EK1101 | 0 | – | P | DC_1 | –V
5V_2 | red | L | EL9190 | 4 | + | P | DC_2 | +V
5VRET_2 | black | L | EL9190 | 4 | – | P | DC_2 | –V
5V_3 | red | L | EL9190 | 8 | + | P | DC_3 | +V
5VRET_3 | black | L | EL9190 | 8 | – | P | DC_3 | –V
5V_4 | red | L | EL9190 | 11 | + | P | DC_4 | +V
5VRET_4 | black | L | EL9190 | 11 | – | P | DC_4 | –V
24V | violet | L | OMRON | DC_2 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_2 | 0V | P | TBLOCK
24V | violet | L | OMRON | DC_3 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_3 | 0V | P | TBLOCK
24V | violet | L | OMRON | DC_4 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_4 | 0V | P | TBLOCK
Coupler
Input | CAT5 | L | EK1101 | 0 | X2 | Comm. | IN
Output | CAT5 | L | EK1101 | 0 | X2 | Comm. | M/0 | X1
Laser Diagnostics
Laser diode 1 power monitor + | green | L | EL3104 | 1 | +I1 | AI | 12 | 1
Laser diode 1 power monitor – | white | L | EL3104 | 1 | –I1 | AI | 12 | 14
Laser diode 2 power monitor + | green | L | EL3104 | 1 | +I2 | AI | 12 | 2
Laser diode 2 power monitor – | white | L | EL3104 | 1 | –I2 | AI | 12 | 15
Laser crystal, TEC error signal + | green | L | EL3104 | 1 | +I3 | AI | 12 | 3
Laser crystal, TEC error signal – | white | L | EL3104 | 1 | –I3 | AI | 12 | 16
Doubling crystal, TEC error signal + | green | L | EL3104 | 1 | +I4 | AI | 12 | 4
Doubling crystal, TEC error signal – | white | L | EL3104 | 1 | –I4 | AI | 12 | 17
Laser diode 1, TEC error signal + | green | L | EL3104 | 2 | +I1 | AI | 12 | 6
Laser diode 1, TEC error signal – | white | L | EL3104 | 2 | –I1 | AI | 12 | 19
Laser diode 2, TEC error signal + | green | L | EL3104 | 2 | +I2 | AI | 12 | 7
Laser diode 2, TEC error signal – | white | L | EL3104 | 2 | –I2 | AI | 12 | 20
Noise eater monitor + | green | L | EL3104 | 2 | +I3 | AI | 12 | 12
Noise eater monitor – | white | L | EL3104 | 2 | –I3 | AI | 12 | 25
| green | L | EL3104 | 2 | +I4 | AI | 12
| white | L | EL3104 | 2 | –I4 | AI | 12
5V_1 | red | L | EL1124 | 3 | + | P | 12 | VCC
5VRET_1 | black | L | EL1124 | 3 | – | P | 12 | GND
Laser diode 1, temp guard | brown | L | EL1124 | 3 | I1 | BI | 12 | 8
Laser diode 2, temp guard | brown | L | EL1124 | 3 | I2 | BI | 12 | 9
Interlock | brown | L | EL1124 | 3 | I3 | BI | 12 | 13
| brown | L | EL1124 | 3 | I4 | BI | 12
LSC Demodulators
RF Mon 1 + | green | L | EL3104 | 5 | +I1 | AI | 11 | 1
RF Mon 1 – | white | L | EL3104 | 5 | –I1 | AI | 11 | 20
LO Mon 1 + | green | L | EL3104 | 5 | +I2 | AI | 11 | 2
LO Mon 1 – | white | L | EL3104 | 5 | –I2 | AI | 11 | 21
RF Mon 2 + | green | L | EL3104 | 5 | +I3 | AI | 11 | 3
RF Mon 2 – | white | L | EL3104 | 5 | –I3 | AI | 11 | 22
LO Mon 2 + | green | L | EL3104 | 5 | +I4 | AI | 11 | 4
LO Mon 2 – | white | L | EL3104 | 5 | –I4 | AI | 11 | 23
RF Mon 3 + | green | L | EL3104 | 6 | +I1 | AI | 11 | 5
RF Mon 3 – | white | L | EL3104 | 6 | –I1 | AI | 11 | 24
LO Mon 3 + | green | L | EL3104 | 6 | +I2 | AI | 11 | 6
LO Mon 3 – | white | L | EL3104 | 6 | –I2 | AI | 11 | 25
RF Mon 4 + | green | L | EL3104 | 6 | +I3 | AI | 11 | 7
RF Mon 4 – | white | L | EL3104 | 6 | –I3 | AI | 11 | 26
LO Mon 4 + | green | L | EL3104 | 6 | +I4 | AI | 11 | 8
LO Mon 4 – | white | L | EL3104 | 6 | –I4 | AI | 11 | 27
5VRET_2 | black | L | EL1124 | 7 | – | P | 11 | 19
OK1 | brown | L | EL1124 | 7 | I1 | BI | 11 | 17
Sign chn 1 | brown | L | EL1124 | 7 | I2 | BI | 11 | 18
Sign chn 2 | brown | L | EL1124 | 7 | I3 | BI | 11 | 37
OK2 | brown | L | EL1124 | 7 | I4 | BI | 11 | 36
RF Amplifiers
Monitor 1 + | green | L | EL3104 | 9 | +I1 | AI | 9 | 12
Monitor 1 – | white | L | EL3104 | 9 | –I1 | AI | 9 | 31
Monitor 2 + | green | L | EL3104 | 9 | +I2 | AI | 9 | 11
Monitor 2 – | white | L | EL3104 | 9 | –I2 | AI | 9 | 30
Monitor 3 + | green | L | EL3104 | 9 | +I3 | AI | 9 | 10
Monitor 3 – | white | L | EL3104 | 9 | –I3 | AI | 9 | 29
Monitor 4 + | green | L | EL3104 | 9 | +I4 | AI | 9 | 9
Monitor 4 – | white | L | EL3104 | 9 | –I4 | AI | 9 | 28
5VRET_3 | black | L | EL1124 | 10 | – | P | 9 | 19
OK1 | brown | L | EL1124 | 10 | I1 | BI | 9 | 37
OK2 | brown | L | EL1124 | 10 | I2 | BI | 9 | 17
OK3 | brown | L | EL1124 | 10 | I3 | BI | 9 | 34
OK4 | brown | L | EL1124 | 10 | I4 | BI | 9 | 14
TCS/Hartmann Sensor
ETM RH Voltage 1 + | green | L | EL3104 | 12 | +I1 | AI | 8 | 1
ETM RH Voltage 1 – | white | L | EL3104 | 12 | –I1 | AI | 8 | 20
ETM RTD Voltage 1 + | green | L | EL3104 | 12 | +I2 | AI | 8 | 2
ETM RTD Voltage 1 – | white | L | EL3104 | 12 | –I2 | AI | 8 | 21
ETM PCB Voltage 1 + | green | L | EL3104 | 12 | +I3 | AI | 8 | 3
ETM PCB Voltage 1 – | white | L | EL3104 | 12 | –I3 | AI | 8 | 22
ETM Current Mon 1 + | green | L | EL3104 | 12 | +I4 | AI | 8 | 4
ETM Current Mon 1 – | white | L | EL3104 | 12 | –I4 | AI | 8 | 23
ETM RH Voltage 2 + | green | L | EL3104 | 13 | +I1 | AI | 8 | 5
ETM RH Voltage 2 – | white | L | EL3104 | 13 | –I1 | AI | 8 | 24
ETM RTD Voltage 2 + | green | L | EL3104 | 13 | +I2 | AI | 8 | 6
ETM RTD Voltage 2 – | white | L | EL3104 | 13 | –I2 | AI | 8 | 25
ETM PCB Voltage 2 + | green | L | EL3104 | 13 | +I3 | AI | 8 | 7
ETM PCB Voltage 2 – | white | L | EL3104 | 13 | –I3 | AI | 8 | 26
ETM Current Mon 2 + | green | L | EL3104 | 13 | +I4 | AI | 8 | 8
ETM Current Mon 2 – | white | L | EL3104 | 13 | –I4 | AI | 8 | 27
ETM Heater Drive 1 + | blue | L | EL4134 | 14 | O1 | AO | 8 | 11
ETM Heater Drive 1 – | yellow | L | EL4134 | 14 | COM | AO | 8 | 30
ETM AWG Heater Drive 1 + | blue | L | EL4134 | 14 | O2 | AO | 8 | 12
ETM AWG Heater Drive 1 – | yellow | L | EL4134 | 14 | COM | AO | 8 | 31
ETM Heater Drive 2 + | blue | L | EL4134 | 14 | O3 | AO | 8 | 13
ETM Heater Drive 2 – | yellow | L | EL4134 | 14 | COM | AO | 8 | 32
ETM AWG Heater Drive 2 + | blue | L | EL4134 | 14 | O4 | AO | 8 | 14
ETM AWG Heater Drive 2 – | yellow | L | EL4134 | 14 | COM | AO | 8 | 33
5VRET_4 | black | L | EL1124 | 15 | – | P | C | 6
Dalsa On/Off | orange | L | EL2124 | 15 | O1 | BO | C | 1
RCX On/Off | orange | L | EL2124 | 15 | O2 | BO | C | 2
| orange | L | EL2124 | 15 | O3 | BO | C
| orange | L | EL2124 | 15 | O4 | BO | C

## Chassis End 2 Middle
End Station Controls Chassis 2 |  | Middle Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | M | OMRON | DC_5 | 24V | P | TBLOCK
0V | gray | M | OMRON | DC_5 | 0V | P | TBLOCK
24V | violet | M | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | M | EK1101 | 0 | 0V | P | TBLOCK
| red | M | EK1101 | 0 | + | P
GND | black | M | EK1101 | 0 | – | P | 7 | 19
5V_5 | red | M | EL9190 | 6 | + | P | DC_5 | +V
5VRET_5 | black | M | EL9190 | 6 | – | P | DC_5 | –V
24V | violet | M | EL9410 | 11 | 24V | P | TBLOCK
0V | gray | M | EL9410 | 11 | 0V | P | TBLOCK
5V_6 | red | M | EL9410 | 11 | + | P | DC_6 | +V
5VRET_6 | black | M | EL9410 | 11 | – | P | DC_6 | –V
Coupler
Output | CAT5 | M | EK1100 | 0 | X2 | Comm. | R/0 | X1
PZT Mirrors
HV10 Monitor PZT 2X + | green | M | EL3104 | 1 | +I1 | AI | 7 | 4
HV10 Monitor PZT 2X – | white | M | EL3104 | 1 | –I1 | AI | 7 | 23
Position Sensor PZT 2X + | green | M | EL3104 | 1 | +I2 | AI | 7 | 3
Position Sensor PZT 2X – | white | M | EL3104 | 1 | –I2 | AI | 7 | 22
HV10 Monitor PZT 2Y + | green | M | EL3104 | 1 | +I3 | AI | 7 | 2
HV10 Monitor PZT 2Y – | white | M | EL3104 | 1 | –I3 | AI | 7 | 21
Position Sensor PZT 2Y + | green | M | EL3104 | 1 | +I4 | AI | 7 | 1
Position Sensor PZT 2Y – | white | M | EL3104 | 1 | –I4 | AI | 7 | 20
HV10 Monitor PZT 1X + | green | M | EL3104 | 2 | +I1 | AI | 7 | 8
HV10 Monitor PZT 1X – | white | M | EL3104 | 2 | –I1 | AI | 7 | 27
Position Sensor PZT 1X + | green | M | EL3104 | 2 | +I2 | AI | 7 | 7
Position Sensor PZT 1X – | white | M | EL3104 | 2 | –I2 | AI | 7 | 26
HV10 Monitor PZT 1Y + | green | M | EL3104 | 2 | +I3 | AI | 7 | 6
HV10 Monitor PZT 1Y – | white | M | EL3104 | 2 | –I3 | AI | 7 | 25
Position Sensor PZT 1Y + | green | M | EL3104 | 2 | +I4 | AI | 7 | 5
Position Sensor PZT 1Y – | white | M | EL3104 | 2 | –I4 | AI | 7 | 24
Photodetector DC Monitors
PD Monitor 1 + | green | M | EL3104 | 3 | +I1 | AI | 7 | 16
PD Monitor 1 – | white | M | EL3104 | 3 | –I1 | AI | 7 | 35
PD Monitor 2 + | green | M | EL3104 | 3 | +I2 | AI | 7 | 15
PD Monitor 2 – | white | M | EL3104 | 3 | –I2 | AI | 7 | 34
PD Monitor 3 + | green | M | EL3104 | 3 | +I3 | AI | 7 | 14
PD Monitor 3 – | white | M | EL3104 | 3 | –I3 | AI | 7 | 33
PD Monitor 4 + | green | M | EL3104 | 3 | +I4 | AI | 7 | 13
PD Monitor 4 – | white | M | EL3104 | 3 | –I4 | AI | 7 | 32
PD Monitor 5 + | green | M | EL3104 | 4 | +I1 | AI | 7 | 12
PD Monitor 5 – | white | M | EL3104 | 4 | –I1 | AI | 7 | 31
PD Monitor 6 + | green | M | EL3104 | 4 | +I2 | AI | 7 | 11
PD Monitor 6 – | white | M | EL3104 | 4 | –I2 | AI | 7 | 30
PD Monitor 7 + | green | M | EL3104 | 4 | +I3 | AI | 7 | 10
PD Monitor 7 – | white | M | EL3104 | 4 | –I3 | AI | 7 | 29
PD Monitor 8 + | green | M | EL3104 | 4 | +I4 | AI | 7 | 9
PD Monitor 8 – | white | M | EL3104 | 4 | –I4 | AI | 7 | 28
Laser Temperature Actuation
Crystal temperature + | blue | M | EL4132 | 5 | O1 | AO | 7 | 18
Crystal temperature – | yellow | M | EL4132 | 5 | COM | AO | 7 | 37
Doubler temperature + | blue | M | EL4132 | 5 | O2 | AO | 7 | 17
Doubler temperature – | yellow | M | EL4132 | 5 | COM | AO | 7 | 36
Auxiliary
5VRET_5 | black | M | EL1124 | 7 | – | P | 6 | 19
Aux BI 1 | brown | M | EL1124 | 7 | I1 | BI | 6 | 23
Aux BI 2 | brown | M | EL1124 | 7 | I2 | BI | 6 | 4
Aux BI 3 | brown | M | EL1124 | 7 | I3 | BI | 6 | 22
Aux BI 4 | brown | M | EL1124 | 7 | I4 | BI | 6 | 3
Aux BO 1 | orange | M | EL2124 | 8 | O1 | BO | 6 | 21
Aux BO 2 | orange | M | EL2124 | 8 | O2 | BO | 6 | 2
Aux BO 2 | orange | M | EL2124 | 8 | O3 | BO | 6 | 20
Aux BO 2 | orange | M | EL2124 | 8 | O4 | BO | 6 | 1
Aux AI 1 + | green | M | EL3104 | 9 | +I1 | AI | 6 | 12
Aux AI 1 – | white | M | EL3104 | 9 | –I1 | AI | 6 | 31
Aux AI 2 + | green | M | EL3104 | 9 | +I2 | AI | 6 | 11
Aux AI 2 – | white | M | EL3104 | 9 | –I2 | AI | 6 | 30
Aux AI 3 + | green | M | EL3104 | 9 | +I3 | AI | 6 | 10
Aux AI 3 – | white | M | EL3104 | 9 | –I3 | AI | 6 | 29
Aux AI 4 + | green | M | EL3104 | 9 | +I4 | AI | 6 | 9
Aux AI 4 – | white | M | EL3104 | 9 | –I4 | AI | 6 | 28
Aux AO 1 + | blue | M | EL4134 | 10 | O1 | AO | 6 | 8
Aux AO 1 – | yellow | M | EL4134 | 10 | COM | AO | 6 | 27
Aux AO 2 + | blue | M | EL4134 | 10 | O2 | AO | 6 | 7
Aux AO 2 – | yellow | M | EL4134 | 10 | COM | AO | 6 | 26
Aux AO 3 + | blue | M | EL4134 | 10 | O3 | AO | 6 | 6
Aux AO 3 – | yellow | M | EL4134 | 10 | COM | AO | 6 | 25
Aux AO 4 + | blue | M | EL4134 | 10 | O4 | AO | 6 | 5
Aux AO 4 – | yellow | M | EL4134 | 10 | COM | AO | 6 | 24
DC PDs ALS table
5VRET_5 | black | M | EL2124 | 12 | – | P | 10 | 19
DC PD1 GAIN0 | orange | M | EL2124 | 12 | O1 | BO | 10 | 7
DC PD1 GAIN1 | orange | M | EL2124 | 12 | O2 | BO | 10 | 26
DC PD2 GAIN0 | orange | M | EL2124 | 12 | O3 | BO | 10 | 8
DC PD2 GAIN1 | orange | M | EL2124 | 12 | O4 | BO | 10 | 27
DC PD3 GAIN0 | orange | M | EL2124 | 13 | O1 | BO | 10 | 3
DC PD3 GAIN1 | orange | M | EL2124 | 13 | O2 | BO | 10 | 22
DC PD4 GAIN0 | orange | M | EL2124 | 13 | O3 | BO | 10 | 4
DC PD4 GAIN1 | orange | M | EL2124 | 13 | O4 | BO | 10 | 23
DC PD1 + | green | M | EL3104 | 14 | +I1 | AI | 10 | 5
DC PD1 – | white | M | EL3104 | 14 | –I1 | AI | 10 | 24
DC PD2 + | green | M | EL3104 | 14 | +I2 | AI | 10 | 6
DC PD2 – | white | M | EL3104 | 14 | –I2 | AI | 10 | 25
DC PD3 + | green | M | EL3104 | 14 | +I3 | AI | 10 | 1
DC PD3 – | white | M | EL3104 | 14 | –I3 | AI | 10 | 20
DC PD4 + | green | M | EL3104 | 14 | +I4 | AI | 10 | 2
DC PD4 – | white | M | EL3104 | 14 | –I4 | AI | 10 | 21

## Chassis End 2 Right
End Station Controls Chassis 2 |  | Right Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | R | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | R | EK1101 | 0 | 0V | P | TBLOCK
24V | violet | R | EK1101 | 0 | + | P | TBLOCK
0V | gray | R | EK1101 | 0 | – | P | TBLOCK
Coupler
Output | CAT5 | R | EK1100 | 0 | X2 | Comm. | OUT
Beam Diverter
24V(*) | violet | R | EL7332 | 1 | + | P | TBLOCK
0V(*) | gray | R | EL7332 | 1 | – | P | TBLOCK
Motor A +(*) | violet | R | EL7332 | 1 | A1 | P | A | 1
Motor A –(*) | gray | R | EL7332 | 1 | A2 | P | A | 6
Motor B + |  | R | EL7332 | 1 | B1 | P
Motor B – |  | R | EL7332 | 1 | B2 | P
Encoder A |  | R | EL7332 | 1 | B1 | P
Encoder B |  | R | EL7332 | 1 | B2 | P
End switch 1 | brown | R | EL1094 | 2 | I1 | BI | A | 2
0V | gray | R | EL1094 | 2 | – | P | A | 7
End switch 2 | brown | R | EL1094 | 2 | I2 | BI | A | 3
0V | gray | R | EL1094 | 2 | – | P | A | 8
|  | R | EL1094 | 2 | I3 | BI
|  | R | EL1094 | 2 | – | P
|  | R | EL1094 | 2 | I4 | BI
|  | R | EL1094 | 2 | – | P
Shutter Control
Shutter A1 Monitor | brown | R | EL1094 | 3 | I1 | BI | B | 5
0V | gray | R | EL1094 | 3 | – | P | B | 8
Shutter A2 Monitor | brown | R | EL1094 | 3 | I2 | BI | B | 13
|  | R | EL1094 | 3 | – | P
|  | R | EL1094 | 3 | I3 | BI
|  | R | EL1094 | 3 | – | P
|  | R | EL1094 | 3 | I4 | BI
|  | R | EL1094 | 3 | – | P
Shutter A1 Close | orange | R | EL2008 | 4 | O1 | BO | B | 6
Shutter A2 Close | orange | R | EL2008 | 4 | O2 | BO | B | 14
Shutter A1 Open | orange | R | EL2008 | 4 | O3 | BO | B | 7
Shutter A2 Open | orange | R | EL2008 | 4 | O4 | BO | B | 15
|  | R | EL2008 | 4 | O5 | BO
|  | R | EL2008 | 4 | O6 | BO
|  | R | EL2008 | 4 | O7 | BO
|  | R | EL2008 | 4 | O8 | BO
Picomotor Controller A (**)
0V | gray | R | EL3102 | 5 | COM | P | TBLOCK
Temperature Monitor 1 + | green | R | EL3102 | 5 | +I1 | AI | 1 | 6
Temperature Monitor 1 – | white | R | EL3102 | 5 | –I1 | AI | 1 | 5
Temperature Monitor 2 + | green | R | EL3102 | 5 | +I2 | AI | 1 | 4
Temperature Monitor 2 – | white | R | EL3102 | 5 | –I2 | AI | 1 | 3
Driver Fault 1 | brown | R | EL1014 | 6 | I1 | BI | 1 | 10
Driver Fault 2 | brown | R | EL1014 | 6 | I2 | BI | 1 | 9
Remote ON | brown | R | EL1014 | 6 | I3 | BI | 1 | 8
Power ON | brown | R | EL1014 | 6 | I4 | BI | 1 | 7
Readbacks | IDC | R | EL1872 | 9 | X1 | BI | 1 | P12
24V | violet | R | EL1872 | 9 | 1 | P | TBLOCK
0V | gray | R | EL1872 | 9 | 2 | P | TBLOCK
Controls | IDC | R | EL2872 | 10 | X1 | BO | 1 | P11
24V | violet | R | EL2872 | 10 | 1 | P | TBLOCK
0V | gray | R | EL2872 | 10 | 2 | P | TBLOCK
Picomotor Controller B (**)
0V | gray | R | EL3102 | 7 | COM | P | TBLOCK
Temperature Monitor 1 + | green | R | EL3102 | 7 | +I1 | AI | 2 | 6
Temperature Monitor 1 – | white | R | EL3102 | 7 | –I1 | AI | 2 | 5
Temperature Monitor 2 + | green | R | EL3102 | 7 | +I2 | AI | 2 | 4
Temperature Monitor 2 – | white | R | EL3102 | 7 | –I2 | AI | 2 | 3
Driver Fault 1 | brown | R | EL1014 | 8 | I1 | BI | 2 | 10
Driver Fault 2 | brown | R | EL1014 | 8 | I2 | BI | 2 | 9
Remote ON | brown | R | EL1014 | 8 | I3 | BI | 2 | 8
Power ON | brown | R | EL1014 | 8 | I4 | BI | 2 | 7
Readbacks | IDC | R | EL1872 | 11 | X1 | BI | 2 | P12
24V | violet | R | EL1872 | 11 | 1 | P | TBLOCK
0V | gray | R | EL1872 | 11 | 2 | P | TBLOCK
Controls | IDC | R | EL2872 | 12 | X1 | BO | 2 | P11
24V | violet | R | EL2872 | 12 | 1 | P | TBLOCK
0V | gray | R | EL2872 | 12 | 2 | P | TBLOCK
* use AWG16 hookup wire
** Terminal order is out-of sequence between the two picomotor controllers (EL1872 and EL2872 are clustered at the end)