***LIGO Laboratory / LIGO Scientific Collaboration***

|  |  |  |  |
| --- | --- | --- | --- |
|

|  |  |  |
| --- | --- | --- |
| T1100529-v1 | *aLIGO* | October 2011 |

 |
| PSL Laser Area Enclosure Air Shower Egress |
| Peter King |

Distribution of this document:

LIGO Scientific Collaboration

This is an internal working note
of the LIGO Laboratory.

|  |  |
| --- | --- |
| **Albert-Einstein-Institut****Callinstraße 38****Hannover, D-30167****Federal Republic of Germany**Phone: (05 11) 762 2229FAX: (05 11) 762 2784 | **California Institute of Technology****LIGO Project, MS 100-36****1200 E. California Blvd.****Pasadena, CA 91125**Phone: (626) 395-2129FAX: (626) 304-9834E-mail: info@ligo.caltech.edu |
| **Laser Zentrum Hannover****Hollerithallee 8****Hannover, D-30419****Federal Republic of Germany**Phone: (05 11) 27 88 0FAX: (05 11) 27 88 100E-mail: info@lzh.de | **Massachusetts Institute of Technology****LIGO Project, NW22-295****185 Albany St.****Cambridge, MA 02139**Phone: (617) 253-4824FAX: (617) 253-7014E-mail: info@ligo.mit.edu |
| **LIGO Hanford Observatory****P.O. Box 159****Richland, WA 99352**Phone: (509) 372-8106FAX: (509) 372-8137 | **LIGO Livingston Observatory****P.O. Box 940****Livingston, LA 70754**Phone: (225) 686-3100FAX: (225) 686-7189 |

<http://www.ligo.caltech.edu>

# Summary

This document lists a retrofit to the air shower that is part of the PSL Laser Area Enclosure. The retrofit is to ensure emergency egress under previously unforeseen circumstances.

# Introduction

The aLIGO PSL at the observatories resides in the Laser Area Enclosure (LAE) within the LVEA. Access to the LAE is via an air shower. To initiate the air shower sequence a button must be pressed. The controller then unlocks the front door. One then enters the air shower, the front door is locked, and the blowers turn on for a short time. When the blowers stop, the rear door is unlocked and one steps into the Ante-Room.

# Air Shower Retrofit

Both observatories have experienced occasions when personnel have been inadvertently trapped in the air shower. To remedy this, a stop button was fitted to the inside of the air shower and Ante-Room that disables the air shower controller, telling it to open both doors of the air shower.

 To ensure emergency egress from the air shower, another retrofit is suggested. A relay shall be installed in the control line to the magnetic latches on the air shower doors. This relay would be activated by hitting the existing stop button(s). This would disable the magnetic latches holding the doors closed. Then both the control logic holding the door closed and the physical mechanism holding the door closed would be disabled, thus allowing the door to be opened.

 Currently both observatories have the stop button. All three installations of the air shower shall have the same retrofit carried out.