## Slide 1: EtherCAT for Advanced LIGO
January 4, 2012
Advanced LIGO
Implementation

## Slide 2: Motivation
Need to replace VME based EPICS system
100’s of slow controls channels (tags) in ISC alone
Vacuum system is still running legacy hardware
Preferably a commercial solution
  High reliability
  Long term availability
  Operator friendly (documentation, external support, etc.)
Separate the computer from analog
  Need a field bus, lot to choose from: Proprietary, Modbus, CANopen, Profibus/ProfiNet, EtherCAT, Sercos III, Ethernet IP, Devicenet, …

## Slide 3: Why EtherCAT?
PSL is using it
Experience in H1 squeezing experiment
Modern design (Ethernet done right)
  100base Ethernet (no expensive backbone)
  Low latency: Datagrams processed on the fly
  Fast: 1-10 ms readout standard; 100us possible
  Software: IEC 61131-3 with EPICS interface
Cost effective for large number of slow channels
  Stackable, DIN-rail mounted units with 1-4 channels typical
  16 bit analog channel: ~$50-$100
  Binary channel: ~$10-$20

## Slide 4: What is EtherCAT?

## Slide 5: What is EtherCAT?
Protocol: (Raw) Ethernet frames
  Memory mapped access (4GB)
  UDP/IP encapsulation possible
Performance
  Real-time kernel on PC
  1000 distributed I/Os in only 30 µs
Topology
  Line, star or tree; hot connect of branches possible
  up to 65,535 devices
  E-bus (LVDS) for DIN mounted modules
  Stand-alone modules (IP67)
Distributed Clock
Special Safety Terminal
Useful information video

## Slide 6: Where does it fit in?
Goal: Run slow controls hardware through EtherCAT
  Mode cleaner board, common mode board, RF distribution system, HWS, picomotors, shutters, timing system readback, etc.
    Slow controls channels are connected to the fast system where it makes sense.
  No VME based systems in the long run
  No stand-alone EPICS RS232/Ethernet/Modbus controls computer
    Need to port legacy systems: dust monitor, weather station, PC/104(?), etc.
    Modbus: Use gateway to EtherCAT, see wiki.
  Boot into the correct state → no burt restore!
EPICS:
  Soft IOC and transport layer
  Screens (medm for now)

## Slide 7: Implementation in Advanced LIGO
Controller: TwinCAT
  Running on rack mounted PCs; 1 controller per building
  Full featured Programmable Logic Controller (PLC)
  OPC and EPICS OPC server for controls interface
IO Chassis
  3U, 24” deep; with 3 DIN rails
  Equipped with EtherCAT Terminals (mostly from Beckhoff)
    Stackable DIN mounted modules
  Field wiring to rear mounted interface connectors
    Mostly D-sub, direct, or
    DB37 to external signal concentrators
Networking
  Fiber between corner and ends (synchronization, data exchange)
  Separate controls network for vertex and ends, see D1102294-v1.

## Slide 8: Long-Haul Connections
MSR
CAT5
MM Fiber
SM Fiber
EY Electronics room
4km
EY CR
EX CR
EX Electronics room
4km
Corner Electronics Room
H2
H1/L1
PTP

## Slide 9: 3U Chassis Design

## Slide 10: 3U Chassis Design

## Slide 11: EtherCAT Coupler
Ethernet
NEXT
IN
E-Bus
Power
E-Bus:
– Ethernet OUT (LVDS)
– Ethernet IN (LVDS)
– 5V Power
Power:
– Positive (24V/5V)
– Ground
– Shield
DIN rail
Coupler requires +24V
to power E-Bus
Separate power for terminals

## Slide 12: EtherCAT Terminal
4-channel binary TTL output
2-channel 16-bit analog input

## Slide 13: Ethernet Configuration
Fiber IN
Fiber OUT
Aux 1
Aux 2
Unconnected ports are automatically closed

## Slide 14: TwinCAT Software (IEC 61131-3)
Real-time task
EtherCAT
Process variables
Shared Memory
PLC:
Periodic
user task
PLC: Periodic
user task
OPC Server
External:EPICS Interface
EPICS
Local user screen

## Slide 15: OPC and the EPICS OPC Server
OPC: Industrial standard for exchanging controls data and events as well as their history
  OPC classic: efficient transport requires Windows DCOM
  OPC UA: modern, platform independent, strong security, information models (i.e., types and hierarchical organization)
  Has been widely adapted by the automation industry A wide selection of software and hardware solutions are available that are supporting it
EPICS OPC Server
  OPC device support maintained at Bessy
Can we run OPC and EPICS in parallel to leverage existing software and also profit from commercial packages?

## Slide 16: Outlook
Deploy the first system in January/February 2012
Easy to expand; easy to add a few more channels
Logic controllers and slow servos can be directly implemented in the TwinCAT PLC
The next TwinCAT will support 64bit OS, multi-core and C++/Matlab
Opens a way forward to adopt commercial solutions

## Slide 17: Further Information
EtherCAT
  EtherCAT Technology Group
  Wikipedia
Hardware and Software
  Beckhoff website
IEC 61131-3:
  R.W. Lewis, “Programming Industrial Control Systems Using IEC 1131-3”
OPC
  OPC Foundation
  EPICS OPC Server