## Slide 1: LLO X-End
CERX
VEAX
PVC – 6” x 10
PVC – 6” Cap
PVC – 6” Cap
¾” QuickEdge
5/8” QuickEdge
6+” hole centered 24” up, 39” over

## Slide 2: VEAX LLO Existing Cable Piers Locations
22.5
22.5
123.0
50.5
64.5
96
94.5
1.5
86.5
205.5
60.0
426.0
331.5
24.0
12.0
88.5
 Corner Station
Cargo Door
 Reference (0)
115.0
Waterfalls
34.0
126.0
Hole
= 10.0 x 10.0
= 4.0 d
Waterfall
41.0
402.0
186.0
36.0

## Slide 3: VEAX LLO Existing Cable Piers Locations
96
1.5
426.0
24.0
12.0
88.5
 Corner Station
Cargo Door
 Reference (0)
115.0
Waterfall
81.0
126.0
Hole
= 10.0 x 10.0
= 4.0 d
402.0
36.0
VE Pump
26 x 56.5
VAC
ISCB4L
72 x 48
144.0
ISC
SUS

## Slide 4: VEAX Overlay
NOTE: This drawing is NOT correct yet. It was made by mirroring the VEAY drawing D1201231-v1. Its ultimate purpose is to show the existing cable tray and piers relative to the as-built IFO.
Things that can be done: (Note: Blue trace is (mostly) existing tray.)
1) Remove old cable tray and pier that interferes with dome parking.
2) Locate L1-ISC-XR1 farther away from existing pier for clearance.
3) Suggest joining basket around BSC to existing cable tray at waterfall.
4) Used removed pier to extend cable tray to L1-ISC-XR1.
5) Add cable tray to reach L1-SUS-YR1.
6) Remove parallel waterfall, move ‘T’ to primary waterfall.
Questions and comments:
1) Where does 11U Short Rack (D1001423-v11) go? (Ignore)
2) Where does L1-AOS-XR1 (if it needs to exist) go? (Does not exist)
3) What does pentagon-2 mean regarding tray removal? Is there tray across the beam tube from L1-SUS-XR1? (Ignore)
4) Is the called-out 10’ height important for some reason? LLO height is 8’. (OK)
5) What are the double doors in the note all about? (Ignore)
6) A door is missing from the garb room to the VEA. (Ignore)
7) The doors are missing from the mechanical room. (Ignore)
8) L1-VAC-XR1 is missing. (Shown)
9) All cabling that currently uses under-beam tray and the waterfall is missing. (Kurt)
10) The Photon Calibrator is missing. (Mounted to tube – part of OPLEV))
11) VE Pumps are not shown. (Shown)
12) Size of ISCB4L is not specified. (72 x 48)
2
3
4
1
5
Existing layout
New layout
6

## Slide 5: CDS Electronics Room X-End (CERX) Rack Layout
<< X-End Racks
(L1-FAC-XC1)
CERX
(L1-VDC-XC1)
(L1-VDC-XC2)
(L1-DAQ-XC1)
(L1-SEI-XC1)
(L1-SUS-XC1)
(L1-SUS-XC2)
(L1-TCS-XC1)
AC Power
Signals and Fiber
DC Power
It is 70’ from the L1-FAC-XC1 Rack to the knee of the waterfall in the VEAX.
The height of the cable trays is 8’.