## Slide 1: Friendly Power Shutdown for LLO Corner Buildings
There are two kinds of power shutdowns: Friendly, meaning we planned it, and Unfriendly, meaning the universe burped. This procedure is intended to identify Friendly power shutdown procedures. Initially, it is incomplete because eventually each subsystem using DC power must provide a procedure for that specific subsystem.

## Slide 2: Power Shutdown Locations
Staging Building Air Conditioners
Mechanical (Chiller) Building MAINS Disconnect
LDAS Air Conditioners
CDS DC Power Supply Transformer Disconnect
Maintenance Room MAINS Disconnect
Control Room Automation Computer
SEC MAINS Disconnect

## Slide 3: Mechanical (Chiller) Building Power Shutdown
1. Shut down the bake ovens in the VPW.
2. Shut down the LDAS computers.
3. Shut down the three air conditioners for the Staging Building.
4. Shut down the three air conditioners for the LDAS room.
5. Turn off the Chillers using the Automation Computer in the Control Room.
6. De-energize the MAINS in the Mechanical Building.
These MAINS in the Mechanical Building control power to:
The Mechanical Building
The Vacuum Processing Warehouse (VPW)
The Staging Building including:
  The High Bay
  The Offices
  The LDAS Room
  HPLF
  The Banquet Room
The House Trailer
<< Locations

## Slide 4: Mechanical (Chiller) Building Power Startup
1. Energize the MAINS in the Mechanical (Chiller) Building.
2. Turn on the Chillers using the Automation Computer in the Control Room.
3. Start up the air conditioners for the LDAS room.
4. Start up the air conditioners for the Staging Building.
5. Start up the LDAS computers.
6. Start up the bake ovens in the VPW.
<< Locations

## Slide 5: Mechanical (Chiller) Building MAINS Disconnect
<< Locations

## Slide 6: Staging Building Air Conditioners
Air Conditioners #2 and #3 is outside, near the air conditioners.
Air Conditioner #1 is inside, in Panel PNL MDP, Circuit ACU #1
<< Locations
<< Shutdown Instructions
<< Startup Instructions

## Slide 7: Staging Building Air Conditioner 1 Disconnect
AC #1 – Use BREAKER to shut off.
<< Staging Building Locations
<< Shutdown Instructions
<< Startup Instructions

## Slide 8: Staging Building Air Conditioners 2 and 3 Disconnects
<< Staging Building Locations
AC #2 – Use DISCONNECT to shut off.
AC #3 – Use DISCONNECT to shut off.
<< Shutdown Instructions
<< Startup Instructions

## Slide 9: LDAS Air Conditioners
<< Locations
<< Shutdown Instructions
<< Startup Instructions

## Slide 10: LDAS Air Conditioning Shutdown
AC #1 – Use CONTROLS to shut down.
AC #2 – De-energize with disconnect switch.
LDAS Air Conditioners
AC #3 – Use CONTROLS to shut down.
<< LDAS Air Conditioners

## Slide 11: LDAS Air Conditioning Startup
AC #1 – Use CONTROLS to start up.
AC #2 – Energize with disconnect switch.
LDAS Air Conditioners
AC #3 – Use CONTROLS to start up.
<< LDAS Air Conditioners

## Slide 12: SEC MAINS Location
SEC MAINS Disconnects
<< Locations
<< Shutdown Instructions
<< Startup Instructions

## Slide 13: SEC MAINS Disconnects
<< SEC MAINS Location
<< Shutdown Instructions
<< Startup Instructions

## Slide 14: SEC MAINS Power Shutdown
1. Turn off power to the LP Panel .
2. Turn off power to the RP Panel .
3. Turn off power to the MP Panel .
<< SEC MAINS Disconnects

## Slide 15: SEC MAINS Power Startup
1. Turn on power to the LP Panel .
2. Turn on power to the RP Panel .
3. Turn on power to the MP Panel .
<< SEC MAINS Disconnects

## Slide 16: Automation System Computer in the Control Room
<< Locations

## Slide 17: Maintenance Room Power Shutdown
1. Ramp down and turn off the LVEA fans using the Automation Computer in the Control Room.
2. Turn off air handler 4 using the Automation Computer in the Control Room.
3. De-energize the DC Transformer breaker switch.
4. De-energize the MAINS in the Maintenance Room.
5. Turn off all subsystem DC supplies. (Optional)
These MAINS in the Maintenance Room control power to:
The Office Support Building (OSB)
The Laser and Vacuum Equipment Area (LVEA)
All computers that are NOT on their own UPS systems, but note that the times for power backup vary considerably.
The Guard Shack
The DC Supplies fall into roughly three categories:
The +12VDC Supplies used for Timing Chassis
The +24VDC Supplies that power IO Extender Chassis
All the rest, which are subsystem dependent
<< Locations

## Slide 18: Maintenance Room Power Startup
1. Energize the MAINS in the Maintenance Room.
2. Energize the DC Transformer breaker switch.
3. Turn on air handler 4 using the Automation Computer in the Control Room.
4. Turn on and ramp up the LVEA fans using the Automation Computer in the Control Room.
5. Turn on DC Power Supplies for each subsystem according to specific procedures for that subsystem. (Optional)
<< Locations

## Slide 19: Maintenance Room MAINS Disconnect
<< Locations

## Slide 20: CDS DC Transformer Breaker Switch
<< Locations

## Slide 21: CPR - DC Power Supplies
<< Locations
PSL
ISC
SUS
SEI
TCS
DAC