## Chassis Corner 6 Left
Corner Station Controls Chassis 6 |  | Left Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | L | OMRON | DC_1 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_1 | 0V | P | TBLOCK
24V | violet | L | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | L | EK1101 | 0 | 0V | P | TBLOCK
5V_1 | red | L | EK1101 | 0 | + | P | DC_1 | +V
5VRET_1 | black | L | EK1101 | 0 | – | P | DC_1 | –V
5V_2 | red | L | EL9190 | 5 | + | P | DC_2 | +V
5VRET_2 | black | L | EL9190 | 5 | – | P | DC_2 | –V
24V | violet | L | EL9410 | 15 | 24V | P | TBLOCK
0V | gray | L | EL9410 | 15 | 0V | P | TBLOCK
5V_3 | red | L | EL9410 | 15 | + | P | DC_3 | +V
5VRET_3 | black | L | EL9410 | 15 | – | P | DC_3 | –V
24V | violet | L | OMRON | DC_2 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_2 | 0V | P | TBLOCK
24V | violet | L | OMRON | DC_3 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_3 | 0V | P | TBLOCK
Coupler
Input | CAT5 | L | EK1101 | 0 | X1 | Comm. | IN
Output | CAT5 | L | EK1101 | 0 | X2 | Comm. | M/0 | X1
RF Amp
Monitor 1 + | green | L | EL3104 | 1 | +I1 | AI | 9 | 12
Monitor 1 – | white | L | EL3104 | 1 | –I1 | AI | 9 | 31
Monitor 2 + | green | L | EL3104 | 1 | +I2 | AI | 9 | 11
Monitor 2 – | white | L | EL3104 | 1 | –I2 | AI | 9 | 30
Monitor 3 + | green | L | EL3104 | 1 | +I3 | AI | 9 | 10
Monitor 3 – | white | L | EL3104 | 1 | –I3 | AI | 9 | 29
Monitor 4 + | green | L | EL3104 | 1 | +I4 | AI | 9 | 9
Monitor 4 – | white | L | EL3104 | 1 | –I4 | AI | 9 | 28
Monitor 5 + | green | L | EL3104 | 2 | +I1 | AI | 9 | 8
Monitor 5 – | white | L | EL3104 | 2 | –I1 | AI | 9 | 27
Monitor 6 + | green | L | EL3104 | 2 | +I2 | AI | 9 | 7
Monitor 6 – | white | L | EL3104 | 2 | –I2 | AI | 9 | 26
Monitor 7 + | green | L | EL3104 | 2 | +I3 | AI | 9 | 6
Monitor 7 – | white | L | EL3104 | 2 | –I3 | AI | 9 | 25
Monitor 8 + | green | L | EL3104 | 2 | +I4 | AI | 9 | 5
Monitor 8 – | white | L | EL3104 | 2 | –I4 | AI | 9 | 24
5VRET_1 | black | L | EL1124 | 3 | – | P | 9 | 19
OK1 | brown | L | EL1124 | 3 | I1 | BI | 9 | 37
OK2 | brown | L | EL1124 | 3 | I2 | BI | 9 | 17
OK3 | brown | L | EL1124 | 3 | I3 | BI | 9 | 34
OK4 | brown | L | EL1124 | 3 | I4 | BI | 9 | 14
OK5 | brown | L | EL1124 | 4 | I1 | BI | 9 | 18
OK6 | brown | L | EL1124 | 4 | I2 | BI | 9 | 35
OK7 | brown | L | EL1124 | 4 | I3 | BI | 9 | 15
OK8 | brown | L | EL1124 | 4 | I4 | BI | 9 | 32
Low Noise VCO w/ PLL B
Monitor 1 + | green | L | EL3104 | 6 | +I1 | AI | 8 | 1
Monitor 1 – | white | L | EL3104 | 6 | –I1 | AI | 8 | 14
Monitor 2 + | green | L | EL3104 | 6 | +I2 | AI | 8 | 2
Monitor 2 – | white | L | EL3104 | 6 | –I2 | AI | 8 | 15
Monitor 3 + | green | L | EL3104 | 6 | +I3 | AI | 8 | 3
Monitor 3 – | white | L | EL3104 | 6 | –I3 | AI | 8 | 16
Temp 1 + | green | L | EL3104 | 6 | +I4 | AI | 8 | 4
Temp 1 – | white | L | EL3104 | 6 | –I4 | AI | 8 | 17
PLL error signal + | green | L | EL3104 | 7 | +I1 | AI | 7 | 1
PLL error signal – | white | L | EL3104 | 7 | –I1 | AI | 7 | 14
PLL control signal + | green | L | EL3104 | 7 | +I2 | AI | 7 | 2
PLL control signal – | white | L | EL3104 | 7 | –I2 | AI | 7 | 15
Tune monitor + | green | L | EL3104 | 7 | +I3 | AI | 8 | 10
Tune monitor – | white | L | EL3104 | 7 | –I3 | AI | 8 | 23
Spare + | green | L | EL3104 | 7 | +I4 | AI | 8 | 12
Spare – | white | L | EL3104 | 7 | –I4 | AI | 8 | 25
Tune adjust + | blue | L | EL4132 | 8 | O1 | AO | 8 | 11
Tune adjust – | yellow | L | EL4132 | 8 | COM | AO | 8 | 24
PLL Offset adjust + | blue | L | EL4132 | 8 | O2 | AO | 7 | 3
PLL Offset adjust – | yellow | L | EL4132 | 8 | COM | AO | 7 | 16
5VRET_2 | black | L | EL1124 | 9 | – | P | 8 | 20
5VRET_2 | black | L | EL1124 | 9 | – | P | 7 | 13
Excitation switch | brown | L | EL1124 | 9 | I1 | BI | 8 | 9
OK | brown | L | EL1124 | 9 | I2 | BI | 8 | 7
PLL OK | brown | L | EL1124 | 9 | I3 | BI | 7 | 25
| brown | L | EL1124 | 9 | I4 | BI
Excitation enable | orange | L | EL2124 | 10 | O1 | BO | 8 | 8
| orange | L | EL2124 | 10 | O2 | BO
PLL input enable | orange | L | EL2124 | 10 | O3 | BO | 7 | 4
PLL sign | orange | L | EL2124 | 10 | O4 | BO | 7 | 17
PLL first compensation | orange | L | EL2124 | 11 | O1 | BO | 7 | 5
PLL second compensation | orange | L | EL2124 | 11 | O2 | BO | 7 | 18
PLL gain slider input 2 bit 0 | orange | L | EL2124 | 11 | O3 | BO | 7 | 6
PLL gain slider input 2 bit 1 | orange | L | EL2124 | 11 | O4 | BO | 7 | 19
PLL gain slider input 2 bit 2 | orange | L | EL2124 | 12 | O1 | BO | 7 | 7
PLL gain slider input 2 bit 3 | orange | L | EL2124 | 12 | O2 | BO | 7 | 20
PLL gain slider input 2 bit 4 | orange | L | EL2124 | 12 | O3 | BO | 7 | 8
PLL gain slider input 2 bit 5 | orange | L | EL2124 | 12 | O4 | BO | 7 | 21
PLL option | orange | L | EL2124 | 13 | O1 | BO | 7 | 9
PLL output enable | orange | L | EL2124 | 13 | O2 | BO | 7 | 22
PLL integrator | orange | L | EL2124 | 13 | O3 | BO | 7 | 10
PLL generic filter | orange | L | EL2124 | 13 | O4 | BO | 7 | 23
PLL VCO filter | orange | L | EL2124 | 14 | O1 | BO | 7 | 11
PLL Low pass | orange | L | EL2124 | 14 | O2 | BO | 7 | 24
PLL Excitation enable | orange | L | EL2124 | 14 | O3 | BO | 7 | 12
| orange | L | EL2124 | 14 | O4 | BO
Low Noise VCO w/ PLL A
Monitor 1 + | green | L | EL3104 | 16 | +I1 | AI | 6 | 1
Monitor 1 – | white | L | EL3104 | 16 | –I1 | AI | 6 | 14
Monitor 2 + | green | L | EL3104 | 16 | +I2 | AI | 6 | 2
Monitor 2 – | white | L | EL3104 | 16 | –I2 | AI | 6 | 15
Monitor 3 + | green | L | EL3104 | 16 | +I3 | AI | 6 | 3
Monitor 3 – | white | L | EL3104 | 16 | –I3 | AI | 6 | 16
Temp 1 + | green | L | EL3104 | 16 | +I4 | AI | 6 | 4
Temp 1 – | white | L | EL3104 | 16 | –I4 | AI | 6 | 17
PLL error signal + | green | L | EL3104 | 17 | +I1 | AI | 5 | 1
PLL error signal – | white | L | EL3104 | 17 | –I1 | AI | 5 | 14
PLL control signal + | green | L | EL3104 | 17 | +I2 | AI | 5 | 2
PLL control signal – | white | L | EL3104 | 17 | –I2 | AI | 5 | 15
Tune monitor + | green | L | EL3104 | 17 | +I3 | AI | 6 | 10
Tune monitor – | white | L | EL3104 | 17 | –I3 | AI | 6 | 23
Spare + | green | L | EL3104 | 17 | +I4 | AI | 6 | 12
Spare – | white | L | EL3104 | 17 | –I4 | AI | 6 | 25
Tune adjust + | blue | L | EL4132 | 18 | O1 | AO | 6 | 11
Tune adjust – | yellow | L | EL4132 | 18 | COM | AO | 6 | 24
PLL Offset adjust + | blue | L | EL4132 | 18 | O2 | AO | 5 | 3
PLL Offset adjust – | yellow | L | EL4132 | 18 | COM | AO | 5 | 16
5VRET_3 | black | L | EL1124 | 19 | – | P | 6 | 20
5VRET_3 | black | L | EL1124 | 19 | – | P | 5 | 13
Excitation switch | brown | L | EL1124 | 19 | I1 | BI | 6 | 9
OK | brown | L | EL1124 | 19 | I2 | BI | 6 | 7
PLL OK | brown | L | EL1124 | 19 | I3 | BI | 5 | 25
| brown | L | EL1124 | 19 | I4 | BI
Excitation enable | orange | L | EL2124 | 20 | O1 | BO | 6 | 8
| orange | L | EL2124 | 20 | O2 | BO
PLL input enable | orange | L | EL2124 | 20 | O3 | BO | 5 | 4
PLL sign | orange | L | EL2124 | 20 | O4 | BO | 5 | 17
PLL first compensation | orange | L | EL2124 | 21 | O1 | BO | 5 | 5
PLL second compensation | orange | L | EL2124 | 21 | O2 | BO | 5 | 18
PLL gain slider input 2 bit 0 | orange | L | EL2124 | 21 | O3 | BO | 5 | 6
PLL gain slider input 2 bit 1 | orange | L | EL2124 | 21 | O4 | BO | 5 | 19
PLL gain slider input 2 bit 2 | orange | L | EL2124 | 22 | O1 | BO | 5 | 7
PLL gain slider input 2 bit 3 | orange | L | EL2124 | 22 | O2 | BO | 5 | 20
PLL gain slider input 2 bit 4 | orange | L | EL2124 | 22 | O3 | BO | 5 | 8
PLL gain slider input 2 bit 5 | orange | L | EL2124 | 22 | O4 | BO | 5 | 21
PLL option | orange | L | EL2124 | 23 | O1 | BO | 5 | 9
PLL output enable | orange | L | EL2124 | 23 | O2 | BO | 5 | 22
PLL integrator | orange | L | EL2124 | 23 | O3 | BO | 5 | 10
PLL generic filter | orange | L | EL2124 | 23 | O4 | BO | 5 | 23
PLL VCO filter | orange | L | EL2124 | 24 | O1 | BO | 5 | 11
PLL Low pass | orange | L | EL2124 | 24 | O2 | BO | 5 | 24
PLL Excitation enable | orange | L | EL2124 | 24 | O3 | BO | 5 | 12
| orange | L | EL2124 | 24 | O4 | BO

## Chassis Corner 6 Middle
Corner Station Controls Chassis 6 |  | Middle Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | M | EK1100 | 0 | 24V | P | TBLOCK
0V | gray | M | EK1100 | 0 | 0V | P | TBLOCK
24V | violet | M | EK1100 | 0 | + | P | TBLOCK
0V | gray | M | EK1100 | 0 | – | P | TBLOCK
Coupler
Output | CAT5 | M | EK1100 | 0 | X2 | Comm. | OUT
Fast Shutter
High Voltage Ready | brown | M | EL1098 | 1 | I1 | BI | 4 | 1
Pulse in Progress | brown | M | EL1098 | 1 | I2 | BI | 4 | 2
Composite Fault | brown | M | EL1098 | 1 | I3 | BI | 4 | 3
Upward Direction Pulse (Blocking Beam) | brown | M | EL1098 | 1 | I4 | BI | 4 | 4
Downward Direction Pulse | brown | M | EL1098 | 1 | I5 | BI | 4 | 5
Spare 1 | brown | M | EL1098 | 1 | I6 | BI | 4 | 6
Spare 2 | brown | M | EL1098 | 1 | I7 | BI | 4 | 7
Spare 3 | brown | M | EL1098 | 1 | I8 | BI | 4 | 8
Shutter Up Command (Block Beam) | orange | M | EL2004 | 2 | O1 | BO | 4 | 9
0V | grey | M | EL2004 | 2 | – | P | 4 | 14
Shutter Down Command (Unblock Beam) | orange | M | EL2004 | 2 | O2 | BO | 4 | 10
|  | M | EL2004 | 2 | – | P | 4 | 15
Spare 1 | orange | M | EL2004 | 2 | O3 | BO | 4 | 11
|  | M | EL2004 | 2 | – | P | 4 | 16
Spare 2 | orange | M | EL2004 | 2 | O4 | BO | 4 | 12
|  | M | EL2004 | 2 | – | P | 4 | 17

## Chassis Corner 6 Right
Corner Station Controls Chassis 6 |  | Right Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin