## Slide 1: Livingston Contamination Control Update
Calum Torrie and Kate Gushwa
On behalf of the Contamination Control Working Group
November 21, 2013

## Slide 2: Outline
Why do we care about contamination?
What is “clean”?
Diagnostic Tools
Mitigation & Protection

## Slide 3: It’s All About Optics
Performance limited by optics
If optics are dirty…
Notes: aLIGO optics are vulnerable to particulate contamination. Surface particles absorb and scatter power from the interferometer mode. Such losses limit recycling and signal cavity finesse, degrading shot-noise limited strain sensitivity.
Refer to Mike Zucker’s paper (see references)
Sensitivity: aLIGO is designed to be sensitive to 10-19 m changes in distance to detect GW.
Cavity Loss Budget: 70 ppm total for all sources between cavity mirrors.
Laser Intensity: Peak Laser Intensities of 200kW/cm2
Absorption, scatter, laser damage to optics and loss to overall sensitivity can/will result from contamination in the vacuum system.
5 ppm/optic Lambertian scatter
  Allow ~2 ppm from dust over ~1 year service interval
    For ε ~ 1: 0.1 ppm absorption is acquired in 6 minutes in a Class 100 cleanroom!
0.5 ppm/optic absorption
  Allow 0.1 ppm from dust over ~1 year service interval
    For ε ~ 1: 0.1 ppm corresponds to a single 30 µm particle in the beam area!

## Slide 4: Defining Clean
Particles per:
Tool:
Requirement:
Cleanroom Class
Volume of air
Particle Counter
ISO 5 (Class 100)
Particulate Cleanliness Level (PCL)
Area of surface
???
Level 65 (optics at full power)
Level 100 (chambers)
Notes: Cleanroom Class:
What we have been using all along to determine cleanliness.
Surface Cleanliness Level:
What we should have been looking at (in addition to Cleanroom Class).
ONE of the tools, but not the only one.

## Slide 5
DIAGNOSTIC TOOLS
Where is it coming from?
How bad is it?

## Slide 6: FBI Samples
Elemental analysis with Scanning Electron Microscope
“Criminals” vs. “Known Suspects”
Carbon Adhesive Tab
Specimen Mount
Plug
Tube
Stainless Steel
Glove
Silver
Sweat
Hair
C3
Notes: Collect samples at observatories of small areas and items of interest. Then sent to Caltech for analysis.
A database for all samples is in progress now.
Hunt for particulates on specimen using INCA software for EDS analysis at a selected point. INCA output:
image
peaks in spectrum
table of elements
Quorum meets to review SEM data. Factors considered:
element weight%
shape
location sampled
history
Identify by:
main element
reference, ex: SSTL
“known suspects”

## Slide 7: FBI Samples on Instrument Surfaces
Group | Material | Specimen | Total
Metals | Any Metal | 63 | 63
Biological | Hair | 1 | 7
 | Skin, Sweat, Saliva | 6 | 
Fibers | C3 | 9 | 28
 | Glove Liner | 2 | 
 | Jeans | 1 | 
 | Unknown Fiber | 4 | 
 | Wipe | 12 | 
Other | In-Vacuum Cable | 2 | 42
 | Carbon | 21 | 
 | Fused Silica | 4 | 
 | Glove | 15 | 
Unknown | Unknown | 25 | 25
Chart: 
| Metals | Biological | Fibers | Other | Unknown
 | 63 | 7 | 28 | 42 | 25
Finding: no smoking gun
Notes: Important notes:
Tendency to collect particulates that are large, out of the ordinary, etc.
Tendency to analyze larger particles on SEM (miss a lot of the small stuff because hard to get a good reading)
Need to analyze more specimen to get a better percentage breakdown of materials.
A database is being created to store all the collected SEM data. Once operational, it will be much easier to compare samples and draw conclusions.
Summary:
Metal was most commonly found. This is not surprising given that most of our parts are metal.
Fairly high amount of carbon, whose source is unknown. Could be partially due to carbon tape on FBI samples.
After metal, we see a lot of C3, wipes, and gloves; suggesting we should re-evaluate our use of these materials.
15% unknowns. We still have a lot to learn.
Biological seems very low at 4% HOWEVER the biological materials tend to be very small (with the exception of hair) and are often overlooked. Have limited time per sample, and tend to focus on big stuff (especially in early SEM sessions). Plus small particles are hard to get a good reading on.

## Slide 8: 4” Wafers & 1” Optics
Notes: W&O placed in chamber vertically and horizontally.
Allow us to collect data on contamination specific to chambers, certain activities (install work, pump down), over time.
Now putting wafers and optics in same locations, so no more apples to oranges comparisons.

## Slide 9: HAM3 Wafers & Optics
Molecular & chemical analysis
Skin dander
Complex mix of hydrocarbons
Mixed silicates (soil)
Polyester & cotton fibers
Notes: Example:
Location:
  T1300103 (wafer) – on +X of table
  T1300109 (optic) – PEEK clamp in front of MC2
In chamber Dec 2012 – Feb 2013
Witnessed pump down and vent, but NO chamber work
BOTH:
  Primary mixed silicates (quartz and mixed cation silicates). Common component of soil tracked into cleanrooms.
  Molecular contamination absorbed on the particulate that is a complex mix of hydrocarbons
  Skin dander
Wafer fibers:
  123x13 microns = degraded polyester
  568x72 microns = cotton

## Slide 10: LHAM2 Wafer PCLs
Chart: Particle diameter (microns)
| 1.954236267845977 | 1.954236267845977
25 | 1 | 10000000
65 | 1 | 10000000
100 | 1 | 10000000
150 | 1 | 10000000
200 | 1 | 10000000
300 | 1 | 10000000
500 | 1 | 10000000
750 | 1 | 10000000
1,000 | 1 | 10000000
1,500 | 1 | 10000000
2,000 | 1 | 10000000
25 | 64.5094 | 22.7623 | 7.6493 | 1 | 0.058369 | 0.012753 | 0.0026587 | 0.00080667 | 0.00013414 | 1.1594e-05 | 1.43e-06 | 2.9897e-07 | 2.9413e-08 | 5.2383e-09
Chart: Particle diameter (microns)
| 1.954236267845977 | 1.954236267845977
25 | 1 | 10000000
65 | 1 | 10000000
100 | 1 | 10000000
150 | 1 | 10000000
200 | 1 | 10000000
300 | 1 | 10000000
500 | 1 | 10000000
750 | 1 | 10000000
1,000 | 1 | 10000000
1,500 | 1 | 10000000
2,000 | 1 | 10000000
25 | 64.5094 | 22.7623 | 7.6493 | 1 | 0.058369 | 0.012753 | 0.0026587 | 0.00080667 | 0.00013414 | 1.1594e-05 | 1.43e-06 | 2.9897e-07 | 2.9413e-08 | 5.2383e-09
Chart: Particle diameter (microns)
| 1.954236267845977 | 1.954236267845977
25 | 1 | 10000000
65 | 1 | 10000000
100 | 1 | 10000000
150 | 1 | 10000000
200 | 1 | 10000000
300 | 1 | 10000000
500 | 1 | 10000000
750 | 1 | 10000000
1,000 | 1 | 10000000
1,500 | 1 | 10000000
2,000 | 1 | 10000000
25 | 64.5094 | 22.7623 | 7.6493 | 1 | 0.058369 | 0.012753 | 0.0026587 | 0.00080667 | 0.00013414 | 1.1594e-05 | 1.43e-06 | 2.9897e-07 | 2.9413e-08 | 5.2383e-09
Chart: Particle diameter (microns)
| 1.954236267845977 | 1.954236267845977
25 | 1 | 10000000
65 | 1 | 10000000
100 | 1 | 10000000
150 | 1 | 10000000
200 | 1 | 10000000
300 | 1 | 10000000
500 | 1 | 10000000
750 | 1 | 10000000
1,000 | 1 | 10000000
1,500 | 1 | 10000000
2,000 | 1 | 10000000
25 | 64.5094 | 22.7623 | 7.6493 | 1 | 0.058369 | 0.012753 | 0.0026587 | 0.00080667 | 0.00013414 | 1.1594e-05 | 1.43e-06 | 2.9897e-07 | 2.9413e-08 | 5.2383e-09
1st pump down – Aug 2012
Most components installed
1 hr basic wipe down
MC1, MC3
462
2nd pump down – Dec 2012
Minimal work (baffles)
2 weeks of clean-as-you-go
X-end mass
PR3
1117
506
3rd pump down – June 2013
Balancing, gluing
1.5 hr wipe down
PR3 (vertical)
Center
393
117
  Iterative cleaning works.

## Slide 11: Particle Evaluation Tool (PET)
Visited National Ignition Facility
New system based on NIF’s design
Entire process performed on-site
Phased implementation starts now
1. Swipe Tool
3. Excel template
2. AmScope
Visited National Ignition Facility
Notes: think of PET as white glove test or the equivalent to a particle counter for surfaces
National Ignition Facility (NIF) is a large laser-based inertial confinement fusion research project.
NIF & LIGO – different goals, but similar concerns. Even tiny amounts of contaminants can damage expensive optics and reduce the amount of laser light that reaches the target (which means less energy on the target, making ignition more difficult)
After being cleaned, NIF optics are always kept in a Class 100 environment or better.
https://dcc.ligo.org/LIGO-D1300697 (tool)
Developed new tool based on NIF design. Prototyped and tested at LLO.
First tools and Amscopes are already at the observatories.

## Slide 12: MITIGATION & PROTECTION

## Slide 13: Scrubs
Body Box testing
  Finding: At least ½ class improvement with scrubs
Chart: Scrubs vs. Street Clothes
| 0.1 | 0.2 | 0.3 | 0.5 | 1 | 5 | 10
ISO 3 (~Class 1) | 1000 | 236.5144 | 101.7625 | 35.1676 | 8.3176 | 0.29251 | 0.069183
ISO 4 (~Class 10) | 10000 | 2365.1441 | 1017.6251 | 351.6757 | 83.1764 | 2.9251 | 0.69183
ISO 5 (~Class 100) | 100000 | 23651.4412 | 10176.2505 | 3516.7572 | 831.7638 | 29.2511 | 6.9183
Calum* - scrubs | 1151.8025 | 437.359 | 162.9909 | 8.1495
Calum - street clothes | 2393.2501 | 567.7517 | 249.9194 | 29.8817 | 2.7165
Margot - scrubs | 228.1873 | 48.8973
Margot - street clothes | 1295.7778 | 133.1093 | 32.5982 | 2.7165
Kate - scrubs | 543.3031 | 149.4083 | 32.5982
Kate - street clothes | 1464.2018 | 505.2719 | 89.645
Total Δ = 19,282 particles
Total Δ = 15,433 particles
Total Δ = 17,340 particles
Notes: Body Box:
Performed series of exercises in an ISO Class 3 box, and particles were collected at knee and sub floor levels. This was done for older and newer garb, with street clothes and scrubs underneath.
People who clean our suits are cleaner than we are.
Exercises weren’t as bad as what we do in chamber.
Scrubs are ESD micro denier polyester.
Found that wearing scrubs, even with older garb, will significantly reduce contamination. For Kate & Margot, it made a difference in cleanroom class. For Calum, it made half a class difference.
Street clothes shed 15,400 – 19,300 more particles than scrubs during test.
In Japanese semiconductor industry, the cleanroom suits have 1 opening- a vent, which attaches to an active exhaust with a small HEPA unit. The HEPA unit is worn at the worker’s waist.

## Slide 14: Glove Washing
Glove testing
  Finding: IPA wash reduces contamination.
How to wash gloves
  Think peanut butter hands

## Slide 15: “Clean-as-you-go”
Wipes
  Chamber & gloves : Vectra Alpha10
  Gross cleaning: Valutek pre-saturated
ANY high purity IPA
  Hand & surfaces
Flashlight arrays
Tiger vacuum cleaners
  Applies to EVERYONE.
End of Work
Assembly
End of Assembly
Post-Install
Pre-Chamber Close
Pre-Install

## Slide 16: “Clean-as-you-go”
End of Work
Assembly
End of Assembly
Post-Install
Pre-Chamber Close
Pre-Install
UV-A inspection light
  NOT around optics
Top Gun ionizer
  Static charge on optic
  Dust on metal surfaces
First Contact
End of Work
Assembly
End of Assembly
Post-Install
Pre-Chamber Close
Pre-Install

## Slide 17: Optimized Transition Area
See Bryan Smith / Matt Heintze for signing out CC tools

## Slide 18: What you should do next…
Set yourself up with basic tools:
Read LIGO-E1201035, Chamber Entry & Exit Guidelines
  Useful checklist
Talk to local the CC reps:
Bryan Smith Gary Traylor
Matt Heintze Danny Sellars
Stuart Aston
Contact Calum Torrie, Margot Phelps, or Kate Gushwa at Caltech if you have further questions:
Office: 626 395 4629
Cell: 626 394 8116 (also on Voxer)
Email: ctorrie@ligo.caltech.edu
Skype: calumiantorrie@skype.com
Are you part of the ______ effort?
Assembly
Install
Commissioning
Operations

## Slide 19: Reminder
LIGO-T1300511 Some thoughts regarding Particulate Contamination Requirements
LIGO-E1201035 Chamber Entry & Exit Guidelines
LIGO-T1300665 The LIGO Particulate Evaluation Tool (PET)
LIGO-T080067 Protecting Installed Optics from Particulates
LIGO-E0900047 aLIGO Contamination Control Plan
LIGO-T1300093 Prudential Body Box Results
LIGO-G1300777 Contamination Control Requirements – Gloves, Cleaning on the Go and The Plan (past, present, and future)
LIGO-G1300427 Slides for Contamination Control
LIGO-T1300493 “Known” Particulate Sample Poster
LIGO-E1201096 Contamination Sample Handling – How to receive, use, send, buy and store samples.
Contamination Control wiki

## Slide 20: The Human Factor (backup)
Chart: Scrubs vs Street Clothes (Total)
| 0.3 | 0.5 | 1
Calum - street clothes | 31112.2507 | 7380.7723 | 3248.9524
Margot - street clothes | 16845.1119 | 1730.4203 | 423.7764
Kate - street clothes | 19034.6233 | 6568.5342 | 1165.3851
Chart: 
| 0.3 | 0.5 | 1
Calum - scrubs | 14973.4328 | 5685.6667 | 2118.882
Margot - scrubs | 2966.4348 | 635.6646 | 0
Kate - scrubs | 7062.94 | 1942.3085 | 423.7764